## Prog Admin (hidden)
Program Administrator Page | Hide this page when distributing for use by program participants

## Lighting Rebate Calculator (hidden)
Lighting Rebate Calculator - Version 1
General Information
Date | [10 empty] | Note: The Rebate Summary Tab provides the calculated energy savings and rebate amounts.
Name
Site Address
Building Age (Yrs) |  |  | Enter the approximate age of the building. Used to determine the age of the lighting system
Lighting Retrofit Description | [14 empty] | Light schedule drop down list |  |  | lightschedhrs_table
[7 empty] | Default Lamp Fixture Description |  |  |  | For Manually Entering Fixture Data |  |  |  | Use default hours for space type
| Enter Space Description |  | Select Space Type |  | Current Fixt. Lamp Type |  | Current Lamp Description |  |  | Qty | Current Fixt. Description | Fixture Wattage |  |  | Light Schedule #1 (1,417 hrs) |  |  |  | Light Schedule #1 | 1416.6665
1 | [14 empty] | Light Schedule #2 (1,860 hrs) |  |  |  | Light Schedule #2 | 1859.9999
| Select Light Operation Schedule |  |  |  | Proposed Fixt. Lamp Type |  | Proposed Lamp Description |  |  | Qty | Proposed Fixt. Description | Fixture Wattage |  |  | Light Schedule #3 (1,989 hrs) |  |  |  | Light Schedule #3 | 1988.6665
Light schedules - for project input table lookup
| Enter Space Description |  | Select Space Type |  | Current Fixt. Lamp Type |  | Current Lamp Description |  |  | Qty | Current Fixt. Description | Fixture Wattage |  | 1
2 | [13 empty] | 2
| Select Light Operation Schedule |  |  |  | Proposed Fixt. Lamp Type |  | Proposed Lamp Description |  |  | Qty | Proposed Fixt. Description | Fixture Wattage |  | 3
4
| Enter Space Description |  | Select Space Type |  | Current Fixt. Lamp Type |  | Current Lamp Description |  |  | Qty | Current Fixt. Description | Fixture Wattage
3
| Select Light Operation Schedule |  |  |  | Proposed Fixt. Lamp Type |  | Proposed Lamp Description |  |  | Qty | Proposed Fixt. Description | Fixture Wattage
| Enter Space Description |  | Select Space Type |  | Current Fixt. Lamp Type |  | Current Lamp Description |  |  | Qty | Current Fixt. Description | Fixture Wattage
4
| Select Light Operation Schedule |  |  |  | Proposed Fixt. Lamp Type |  | Proposed Lamp Description |  |  | Qty | Proposed Fixt. Description | Fixture Wattage
Light Schedules - For estimating lighting operating hours when default operating hours are not used
Up to three light schedules may be created. Scroll down to enter or modify a light schedule.
| Light Schedule #1 | [6 empty] | Annual run-time (hrs) | 1416.6665 |  |  |  | Operating hour calculations | [7 empty] | Month drop down menu control for season 2 and 3
| Does the light schedule vary during different times of the year? |  |  |  |  | Yes | [15 empty] | Range name: season2 and season3 (dynamic ranges)
If yes, up to 3 seasonal schedules may be entered
| Enter the number of seasonal schedules |  |  | 1 | [18 empty] | Light schedule 1
[22 empty] | 0 | 6 | Offset for defining season2 range
| Season #1 |  |  | Season #2 |  |  | Season #3 | [6 empty] | 12 | sum of entered months - if greater than 12, months are automatically reduced in op hr calculation | [6 empty] | 1 | 5 | Offset for defining season3 range
| # of Months | 7 |  | # of Months | 1 |  | # of Months | 4 | [5 empty] | 7 | 1 | 4 | seasonal months adjusted if sum exceeds 12 |  |  |  |  | 2
| Warning: the number of months entered exceeds 12 | [15 empty] | protects from overestimating savings due to dynamic lookup function error |  |  |  |  | 3 | Light schedule 2
| Weekly Schedule | [12 empty] | Calculated daily op hrs | [7 empty] | 4 | 3 | Offset for defining season2 range
|  | Time On | Time Off |  | Time On | Time Off |  | Time On | Time Off |  |  |  |  | seas1 hrs | seas 2 hrs | seas3 hrs | [5 empty] | 5 | 1 | Offset for defining season3 range
| Mon | 7:00 | 17:00 | Mon | Off |  | Mon | Off | [5 empty] | 10 | 0 | 0 | [5 empty] | 6
| Tue | 7:00 | 17:00 | Tue | Off |  | Tue | Off | [5 empty] | 10 | 0 | 0 | [5 empty] | 7 | Light schedule 3
| Wed | 7:00 | 17:00 | Wed | Off |  | Wed | Off | [5 empty] | 10 | 0 | 0 | [5 empty] | 8 | 4 | Offset for defining season2 range
| Thu | 7:00 | 17:00 | Thu | Off |  | Thu | Off | [5 empty] | 10 | 0 | 0 | [5 empty] | 9 | 2 | Offset for defining season3 range
| Fri | 7:00 | 17:00 | Fri | Off |  | Fri | Off | [5 empty] | 10 | 0 | 0 | [5 empty] | 10
| Sat | Off |  | Sat | Off |  | Sat | Off | [5 empty] | 0 | 0 | 0 | [5 empty] | 11
| Sun | Off | 0:30 | Sun | Off |  | Sun | Off | [5 empty] | 0 | 0 | 0 | [5 empty] | 12
| # of Holidays | 10 |  | # of Holidays | 0 |  | # of Holidays | 0 |  |  |  |  | Weekly hrs | 50 | 0 | 0
| Note: lights are assumed off during holidays. Entering holidays reduces the annual operating hours | [11 empty] | Annual hrs | 1416.6665 | 0 | 0 | 1416.6665 | Sum of annual hours - controlled by # of seasons entry.
| Light Schedule #2 | [6 empty] | Annual run-time (hrs) | 1859.9999
| Does the light schedule vary during different times of the year? |  |  |  |  | Yes
If yes, up to 3 seasonal schedules may be entered
| Enter the number of seasonal schedules |  |  | 3
| Season #1 |  |  | Season #2 |  |  | Season #3 | [6 empty] | 12 | sum of entered months - if greater than 12, months are automatically reduced in op hr calculation
| # of Months | 10 |  | # of Months | 2 |  | # of Months | 0 | [5 empty] | 10 | 2 | 0 | seasonal months adjusted if sum exceeds 12
| Warning: the number of months entered exceeds 12 | [15 empty] | protects from overestimating savings due to dynamic lookup function error
| Weekly Schedule | [12 empty] | Calculated daily op hrs
|  | Time On | Time Off |  | Time On | Time Off |  | Time On | Time Off |  |  |  |  | seas1 hrs | seas 2 hrs | seas3 hrs
| Mon | 8:00 | 17:00 | Mon | Off |  | Mon | Off | [5 empty] | 9 | 0 | 0
| Tue | 8:00 | 17:00 | Tue | Off |  | Tue | Off | [5 empty] | 9 | 0 | 0
| Wed | 8:00 | 17:00 | Wed | Off |  | Wed | Off | [5 empty] | 9 | 0 | 0
| Thu | 8:00 | 17:00 | Thu | Off |  | Thu | Off | [5 empty] | 9 | 0 | 0
| Fri | 8:00 | 17:00 | Fri | Off |  | Fri | Off | [5 empty] | 9 | 0 | 0
| Sat | Off |  | Sat | Off |  | Sat | Off | [5 empty] | 0 | 0 | 0
| Sun | Off |  | Sun | Off |  | Sun | Off | [5 empty] | 0 | 0 | 0
| # of Holidays | 10 |  | # of Holidays | 0 |  | # of Holidays | 0 |  |  |  |  | Weekly hrs | 45 | 0 | 0
| Note: lights are assumed off during holidays. Entering holidays reduces the annual operating hours | [11 empty] | Annual hrs | 1859.9999 | 0 | 0 | 1859.9999 | Sum of annual hours - controlled by # of seasons entry.
| Light Schedule #3 | [6 empty] | Annual run-time (hrs) | 1988.6665
| Does the light schedule vary during different times of the year? |  |  |  |  | Yes
If yes, up to 3 seasonal schedules may be entered
| Enter the number of seasonal schedules |  |  | 3
| Season #1 |  |  | Season #2 |  |  | Season #3 | [6 empty] | 12 | sum of entered months - if greater than 12, months are automatically reduced in op hr calculation
| # of Months | 9 |  | # of Months | 2 |  | # of Months | 1 | [5 empty] | 9 | 2 | 1 | seasonal months adjusted if sum exceeds 12
| Warning: the number of months entered exceeds 12 | [15 empty] | protects from overestimating savings due to dynamic lookup function error
| Weekly Schedule | [12 empty] | Calculated daily op hrs
|  | Time On | Time Off |  | Time On | Time Off |  | Time On | Time Off |  |  |  |  | seas1 hrs | seas 2 hrs | seas3 hrs
| Mon | 7:00 | 17:00 | Mon | 8:00 | 12:00 | Mon | Off | [5 empty] | 10 | 4 | 0
| Tue | 7:00 | 17:00 | Tue | 8:00 | 12:00 | Tue | Off | [5 empty] | 10 | 4 | 0
| Wed | 7:00 | 17:00 | Wed | 8:00 | 12:00 | Wed | Off | [5 empty] | 10 | 4 | 0
| Thu | 7:00 | 17:00 | Thu | 8:00 | 12:00 | Thu | Off | [5 empty] | 10 | 4 | 0
| Fri | 7:00 | 17:00 | Fri | Off |  | Fri | Off | [5 empty] | 10 | 0 | 0
| Sat | Off |  | Sat | Off |  | Sat | Off | [5 empty] | 0 | 0 | 0
| Sun | Off |  | Sun | Off |  | Sun | Off | [5 empty] | 0 | 0 | 0
| # of Holidays | 10 |  | # of Holidays | 0 |  | # of Holidays | 0 |  |  |  |  | Weekly hrs | 50 | 16 | 0
| Note: lights are assumed off during holidays. Entering holidays reduces the annual operating hours | [11 empty] | Annual hrs | 1849.9998 | 138.6667 | 0 | 1988.6665 | Sum of annual hours - controlled by # of seasons entry.
Note on D10: A space type must be selected.
Note on F10: Additional Information: This cell locks after a lamp description is entered. To re-select the fixture lamp type, delete the lamp description. Definitions: User-defined: Indicates the lamp type and wattage will be entered manually T8_HP_4ft: T8 linear fluorescent lamp rated as high performance by Consortium for Energy Efficiency (CEE) HPS: high pressure sodium MH: metal halide
Note on M10: To manually enter fixture data, select "User-defined" as the fixture lamp type
Note on N10: Fixture Wattage: Enter the total wattage for the entire fixture as specified by the manufacturer. Supporting documentation is required.
Note on B12: Lighting Operating Hours: Use default operating hours for the space type, or estimate the space operating hours by using one of the three light schedule tables below. If a light schedule is revised, reselect it so that the operating hours shown with the name are updated.
Note on F12: Additional Information: This cell locks after a lamp description is entered. To re-select the fixture lamp type, delete the lamp description. Definitions: User-defined: Indicates the lamp type and wattage will be entered manually T8_HP_4ft: T8 linear fluorescent lamp rated as high performance by Consortium for Energy Efficiency (CEE) HPS: high pressure sodium MH: metal halide
Note on M12: To manually enter fixture data, select "User-defined" as the fixture lamp type
Note on N12: Fixture Wattage: Enter the total wattage for the entire fixture as specified by the manufacturer. Supporting documentation is required.
Note on D15: A space type must be selected.
Note on F15: Additional Information: This cell locks after a lamp description is entered. To re-select the fixture lamp type, delete the lamp description. Definitions: User-defined: Indicates the lamp type and wattage will be entered manually T8_HP_4ft: T8 linear fluorescent lamp rated as high performance by Consortium for Energy Efficiency (CEE) HPS: high pressure sodium MH: metal halide
Note on M15: To manually enter fixture data, select "User-defined" as the fixture lamp type
Note on N15: Fixture Wattage: Enter the total wattage for the entire fixture as specified by the manufacturer. Supporting documentation is required.
Note on B17: Lighting Operating Hours: Use default operating hours for the space type, or estimate the space operating hours by using one of the three light schedule tables below. If a light schedule is revised, reselect it so that the operating hours shown with the name are updated.
Note on F17: Additional Information: This cell locks after a lamp description is entered. To re-select the fixture lamp type, delete the lamp description. Definitions: User-defined: Indicates the lamp type and wattage will be entered manually T8_HP_4ft: T8 linear fluorescent lamp rated as high performance by Consortium for Energy Efficiency (CEE) HPS: high pressure sodium MH: metal halide
Note on M17: To manually enter fixture data, select "User-defined" as the fixture lamp type
Note on N17: Fixture Wattage: Enter the total wattage for the entire fixture as specified by the manufacturer. Supporting documentation is required.
Note on D20: A space type must be selected
Note on F20: Additional Information: This cell locks after a lamp description is entered. To re-select the fixture lamp type, delete the lamp description. Definitions: User-defined: Indicates the lamp type and wattage will be entered manually T8_HP_4ft: T8 linear fluorescent lamp rated as high performance by Consortium for Energy Efficiency (CEE) HPS: high pressure sodium MH: metal halide
Note on M20: To manually enter fixture data, select "User-defined" as the fixture lamp type
Note on N20: Fixture Wattage: Enter the total wattage for the entire fixture as specified by the manufacturer. Supporting documentation is required.
Note on B22: Lighting Operating Hours: Use default operating hours for the space type, or estimate the space operating hours by using one of the three light schedule tables below. If a light schedule is revised, reselect it so that the operating hours shown with the name are updated.
Note on F22: Additional Information: This cell locks after a lamp description is entered. To re-select the fixture lamp type, delete the lamp description. Definitions: User-defined: Indicates the lamp type and wattage will be entered manually T8_HP_4ft: T8 linear fluorescent lamp rated as high performance by Consortium for Energy Efficiency (CEE) HPS: high pressure sodium MH: metal halide
Note on M22: To manually enter fixture data, select "User-defined" as the fixture lamp type
Note on N22: Fixture Wattage: Enter the total wattage for the entire fixture as specified by the manufacturer. Supporting documentation is required.
Note on D25: A space type must be selected.
Note on F25: Additional Information: This cell locks after a lamp description is entered. To re-select the fixture lamp type, delete the lamp description. Definitions: User-defined: Indicates the lamp type and wattage will be entered manually T8_HP_4ft: T8 linear fluorescent lamp rated as high performance by Consortium for Energy Efficiency (CEE) HPS: high pressure sodium MH: metal halide
Note on M25: To manually enter fixture data, select "User-defined" as the fixture lamp type
Note on N25: Fixture Wattage: Enter the total wattage for the entire fixture as specified by the manufacturer. Supporting documentation is required.
Note on B27: Lighting Operating Hours: Use default operating hours for the space type, or estimate the space operating hours by using one of the three light schedule tables below. If a light schedule is revised, reselect it so that the operating hours shown with the name are updated.
Note on F27: Additional Information: This cell locks after a lamp description is entered. To re-select the fixture lamp type, delete the lamp description. Definitions: User-defined: Indicates the lamp type and wattage will be entered manually T8_HP_4ft: T8 linear fluorescent lamp rated as high performance by Consortium for Energy Efficiency (CEE) HPS: high pressure sodium MH: metal halide
Note on M27: To manually enter fixture data, select "User-defined" as the fixture lamp type
Note on N27: Fixture Wattage: Enter the total wattage for the entire fixture as specified by the manufacturer. Supporting documentation is required.

## Rebate Summary (hidden)
Rebate Calculator - Project Summary Page
Date |  |  | 0 | [9 empty] | KWh Savings |  |  | 0
Customer Name |  |  | 0 | [9 empty] | Peak kW Reduction |  |  | 0 |  | Title 24 Adjustment Calculation
Site Address |  |  | 0 | [9 empty] | Rebate Amount |  |  | 0 |  | Adjustments are based on retrofit types that are most likely to be affected by Title24 lighting alteration requirements
Building Age |  |  | 0 | [14 empty] | Note: for preexisting T12 fixtures, a T8 equiv. is used as the baseline. For a 4 ft lamp, the resulting baseline power reduction is 28-42%.
Note: for outdoor lighting, the default operating hours are 3,490, which accounts for new control requirements.
|  |  | Current Lighting |  | Proposed Lighting
Space Description | Space end use type | Space ID | Qty | Lamp Type | Meas Qty | New Lamp Type | New Control Type | kWh Savings | Peak kW Re-duction | Control Savings | User-Defined Control Savings? | Are occupancy or motion sensors mandatory? | Op Hrs | Op Hrs - Default or User Input? | Title 24 LPA Baseline Used? | Rebate Amount | Negative Therms Impact | Greater than 40 fixtures? | LT type in list? | Bldg age> 10? | Savings reduction applied
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% |  |  | 0 |  |  | 0 | 0 | No | No | No | None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% |  |  | 0 |  |  | 0 | 0 | No | No | No | None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% |  |  | 0 |  |  | 0 | 0 | No | No | No | None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% |  |  | 0 |  |  | 0 | 0 | No | No | No | None
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% |  |  | 0 |  |  | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% |  |  | 0 |  |  | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% |  |  | 0 |  |  | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% |  |  | 0 |  |  | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% |  |  | 0 |  |  | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% |  |  | 0 |  |  | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% |  |  | 0 |  |  | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% |  |  | 0 |  |  | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% |  |  | 0 |  |  | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% |  |  | 0 |  |  | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% |  |  | 0 |  |  | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% |  |  | 0 |  |  | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% |  |  | 0 |  |  | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% |  |  | 0 |  |  | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% |  |  | 0 |  |  | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% |  |  | 0 |  |  | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% |  |  | 0 |  |  | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% |  |  | 0 |  |  | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% |  |  | 0 |  |  | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% |  |  | 0 |  |  | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% |  |  | 0 |  |  | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% |  |  | 0 |  |  | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% |  |  | 0 |  |  | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% |  |  | 0 |  |  | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% |  |  | 0 |  |  | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% |  |  | 0 |  |  | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% |  |  | 0 |  |  | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% |  |  | 0 |  |  | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% |  |  | 0 |  |  | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% |  |  | 0 |  |  | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% |  |  | 0 |  |  | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% |  |  | 0 |  |  | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% |  |  | 0 |  |  | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% |  |  | 0 |  |  | 0 | 0
Total |  |  | 0 |  | 0 |  |  | 0 | 0 | [6 empty] | 0 | 0
Note: Savings and rebate amounts will be not be reported if there is missing information in the Lighting Rebate Calculator. For each measure, verify a space use type and proposed lighting quantity and lamp type have been correctly entered. | [18 empty] | Light type likely to be affected by code requirements
T8_4ft
T8_all_other_lengths
T12_Lamp
HPS
MH
User-defined
Title 24 adjustment factor - accounts for likely reduction in baseline power due to LPA and control requirements
[19 empty] | Bldg <10 adj | Bldg >10 adj
[19 empty] | 0% | 0% | from program admin tab

## Instructions
TRM 400 - Lighting Savings Calculator (Revised 10/1/2017)
Technical Reference Manual: Semi-Custom Measure
Introduction
The lighting savings calculator is used to estimate energy savings and determine rebate amounts for energy efficient lighting measures. The calculator consists of two input tables, two summary reports, and an output report for early retirement measures. It contains a lighting fixture database and reference data that are used in the tables to estimate measure energy savings. For projects using a natural replacement code baseline, the TRM 408 (interior lighting) and TRM 409 (exterior lighting) savings calculators may be used to estimate savings.
Instructions for Use
1 | Enter lighting operating hour schedules
In the Project Input Table, enter a space description and select a space use type. The space end use type will determine the default lighting operating hours and control savings factors that are available for estimating energy savings.
2 | Optional - Enter lighting operating hour schedules
If user-input operating hours will be used, up to six lighting schedules may be entered in the Operating Schedules tab. The applicable lighting schedule can be selected in the Project Input Table.
3 | Enter lighting fixture quantities and existing lighting control type
Select the existing control type - for occupancy sensor and manual bi-level controls, the control savings factor will be applied to the pre-existing fixture energy use.
4 | Input pre-existing fixture types
Select default fixture lamp type, or select "user-defined" to manually enter fixture description and wattage.
For default fixture lamp types, select the lamp description. Note this selection is based on the default lamp type selected. If you select a lamp description and then re-select a lamp type, you must also re-select the lamp description (otherwise the calculations will return #N/A). The cell will be highlighted in yellow if the lamp type does not match the fixture type.
For manually-entered fixtures, provide a fixture/lamp description and the rated fixture wattage.
5 | Input energy efficient lighting measure (new or proposed lighting fixture)
If the quantity of fixtures will change as part of the retrofit, enter the new fixture quantity.
If new controls will be installed, select control type from drop down menu. If control type is not available or measured data is used to estimate custom control savings, select User-defined savings from the drop down menu and enter the control savings factor.
Select default fixture lamp type, or select "user-defined" to manually enter fixture description and wattage. Note that LED fixture/lamp wattages are entered in the "user-defined" section
6 | Project Summary and Inventory Reports
The project input, project summary, and inventory report tables are sized to show the results for 38 measures. If the project has more than 38 measures, then the table will need to be expanded. To expand the tables, unprotect the worksheet and:
| a | Select any row in the table, then select the Table Tools menu (appears above the Design menu)
| b | Turn off Total Row
| c | Drag the last cell in column A of the table down until sufficient rows are added
| d | The table - including all calculated cells - will automatically expand
| e | Turn on Total Row
7 | Early Retirement Reporting
The early retirement reporting tab provides the necessary inputs for reporting early retirement lighting retrofit projects into the E3 reporting tool. The only input needed is the full measure cost (equipment and installation). Default EUL values may be over-written with measure-specific EUL values.
8 | Rebate Calculation
| To calculate rebates, enter the incentive level: |  | 0.15 | $/kWh

## Project Input Table
| Project name | [17 empty] | This section no longer used
| Climate zone | CZ03 | [21 empty] | kWh savings | kW red | % savings | [15 empty] | Rebate |  | Therms
| Date | [20 empty] | 0 | 0 | 0 | 0 | #DIV/0! |  |  | 0 | 0 | [11 empty] | 0 |  | 0
[8 empty] | Pre-existing conditions |  |  |  | Efficient conditions (EC) - the proposed or newly installed lighting | [6 empty] | Baseline assessment |  |  | Energy Savings Summary |  |  |  |  | Energy Savings Calculation | [13 empty] | Rebate Calculation |  | Nat. Gas IE
Num | Space Description | Space end use type | Fixture Quantity | Existing Control Type | Operating Hours-Default | Select Operating Schedule | Operating Hours | Fixture Lamp Type | Lamp Description (Default List) | Fixture Wattage (for user-defined fixtures) | Fixture Description (only needed if user-defined) | Revised Fixture Quantity (enter only if fixture count changes) | Control Type | User-Defined Control Savings Factor | New Lamp Type | Lamp Descrip. | Fixture_Wattage (for LED or User-Defined Lamp Type) | Fixture_Description (for LED or User-Defined Lamp Type) | Fixture Replacement or Fixture Retrofit | Enter Space ID | Space Use Type (from T24 analysis table) | kWh baseline | kWh efficient | kWh savings | Peak kW reduction | % kWh Savings | kW pre-existing | KW code adj factor | kW baseline | kW efficient | operating hours2 | Mandatory OC or motion sensors? | baseline control adj factor | EC control % savings factor | HVAC IE Energy factor | HVAC IE Demand Factor | Coincident Demand Factor (CDF) | Efficient Fixture Qty | Baseline fixture lookup | Efficient fixture lookup | Incentive Level ($/kWh) | Rebate $ | HVAC IE factor Therms/kWh | Therms
1 | [21 empty] | 0 | 0 | 0 | 0 | 0% | 0 | 1 | 0 | 0 | 0 | No | 0% | 0% | 1 | 1 | 1 | 0 |  |  | 0.15 | 0 | 0 | 0
2 | [21 empty] | 0 | 0 | 0 | 0 | 0% | 0 | 1 | 0 | 0 | 0 | No | 0% | 0% | 1 | 1 | 1 | 0 |  |  | 0.15 | 0 | 0 | 0
3 | [21 empty] | 0 | 0 | 0 | 0 | 0% | 0 | 1 | 0 | 0 | 0 | No | 0% | 0% | 1 | 1 | 1 | 0 |  |  | 0.15 | 0 | 0 | 0
4 | [21 empty] | 0 | 0 | 0 | 0 | 0% | 0 | 1 | 0 | 0 | 0 | No | 0% | 0% | 1 | 1 | 1 | 0 |  |  | 0.15 | 0 | 0 | 0
5 | [21 empty] | 0 | 0 | 0 | 0 | 0% | 0 | 1 | 0 | 0 | 0 | No | 0% | 0% | 1 | 1 | 1 | 0 |  |  | 0.15 | 0 | 0 | 0
6 | [21 empty] | 0 | 0 | 0 | 0 | 0% | 0 | 1 | 0 | 0 | 0 | No | 0% | 0% | 1 | 1 | 1 | 0 |  |  | 0.15 | 0 | 0 | 0
7 | [21 empty] | 0 | 0 | 0 | 0 | 0% | 0 | 1 | 0 | 0 | 0 | No | 0% | 0% | 1 | 1 | 1 | 0 |  |  | 0.15 | 0 | 0 | 0
8 | [21 empty] | 0 | 0 | 0 | 0 | 0% | 0 | 1 | 0 | 0 | 0 | No | 0% | 0% | 1 | 1 | 1 | 0 |  |  | 0.15 | 0 | 0 | 0
9 | [21 empty] | 0 | 0 | 0 | 0 | 0% | 0 | 1 | 0 | 0 | 0 | No | 0% | 0% | 1 | 1 | 1 | 0 |  |  | 0.15 | 0 | 0 | 0
10 | [21 empty] | 0 | 0 | 0 | 0 | 0% | 0 | 1 | 0 | 0 | 0 | No | 0% | 0% | 1 | 1 | 1 | 0 |  |  | 0.15 | 0 | 0 | 0
11 | [21 empty] | 0 | 0 | 0 | 0 | 0% | 0 | 1 | 0 | 0 | 0 | No | 0% | 0% | 1 | 1 | 1 | 0 |  |  | 0.15 | 0 | 0 | 0
12 | [21 empty] | 0 | 0 | 0 | 0 | 0% | 0 | 1 | 0 | 0 | 0 | No | 0% | 0% | 1 | 1 | 1 | 0 |  |  | 0.15 | 0 | 0 | 0
13 | [21 empty] | 0 | 0 | 0 | 0 | 0% | 0 | 1 | 0 | 0 | 0 | No | 0% | 0% | 1 | 1 | 1 | 0 |  |  | 0.15 | 0 | 0 | 0
14 | [21 empty] | 0 | 0 | 0 | 0 | 0% | 0 | 1 | 0 | 0 | 0 | No | 0% | 0% | 1 | 1 | 1 | 0 |  |  | 0.15 | 0 | 0 | 0
15 | [21 empty] | 0 | 0 | 0 | 0 | 0% | 0 | 1 | 0 | 0 | 0 | No | 0% | 0% | 1 | 1 | 1 | 0 |  |  | 0.15 | 0 | 0 | 0
16 | [21 empty] | 0 | 0 | 0 | 0 | 0% | 0 | 1 | 0 | 0 | 0 | No | 0% | 0% | 1 | 1 | 1 | 0 |  |  | 0.15 | 0 | 0 | 0
17 | [21 empty] | 0 | 0 | 0 | 0 | 0% | 0 | 1 | 0 | 0 | 0 | No | 0% | 0% | 1 | 1 | 1 | 0 |  |  | 0.15 | 0 | 0 | 0
18 | [21 empty] | 0 | 0 | 0 | 0 | 0% | 0 | 1 | 0 | 0 | 0 | No | 0% | 0% | 1 | 1 | 1 | 0 |  |  | 0.15 | 0 | 0 | 0
19 | [21 empty] | 0 | 0 | 0 | 0 | 0% | 0 | 1 | 0 | 0 | 0 | No | 0% | 0% | 1 | 1 | 1 | 0 |  |  | 0.15 | 0 | 0 | 0
20 | [21 empty] | 0 | 0 | 0 | 0 | 0% | 0 | 1 | 0 | 0 | 0 | No | 0% | 0% | 1 | 1 | 1 | 0 |  |  | 0.15 | 0 | 0 | 0
21 | [21 empty] | 0 | 0 | 0 | 0 | 0% | 0 | 1 | 0 | 0 | 0 | No | 0% | 0% | 1 | 1 | 1 | 0 |  |  | 0.15 | 0 | 0 | 0
22 | [21 empty] | 0 | 0 | 0 | 0 | 0% | 0 | 1 | 0 | 0 | 0 | No | 0% | 0% | 1 | 1 | 1 | 0 |  |  | 0.15 | 0 | 0 | 0
23 | [21 empty] | 0 | 0 | 0 | 0 | 0% | 0 | 1 | 0 | 0 | 0 | No | 0% | 0% | 1 | 1 | 1 | 0 |  |  | 0.15 | 0 | 0 | 0
24 | [21 empty] | 0 | 0 | 0 | 0 | 0% | 0 | 1 | 0 | 0 | 0 | No | 0% | 0% | 1 | 1 | 1 | 0 |  |  | 0.15 | 0 | 0 | 0
25 | [21 empty] | 0 | 0 | 0 | 0 | 0% | 0 | 1 | 0 | 0 | 0 | No | 0% | 0% | 1 | 1 | 1 | 0 |  |  | 0.15 | 0 | 0 | 0
26 | [21 empty] | 0 | 0 | 0 | 0 | 0% | 0 | 1 | 0 | 0 | 0 | No | 0% | 0% | 1 | 1 | 1 | 0 |  |  | 0.15 | 0 | 0 | 0
27 | [21 empty] | 0 | 0 | 0 | 0 | 0% | 0 | 1 | 0 | 0 | 0 | No | 0% | 0% | 1 | 1 | 1 | 0 |  |  | 0.15 | 0 | 0 | 0
28 | [21 empty] | 0 | 0 | 0 | 0 | 0% | 0 | 1 | 0 | 0 | 0 | No | 0% | 0% | 1 | 1 | 1 | 0 |  |  | 0.15 | 0 | 0 | 0
29 | [21 empty] | 0 | 0 | 0 | 0 | 0% | 0 | 1 | 0 | 0 | 0 | No | 0% | 0% | 1 | 1 | 1 | 0 |  |  | 0.15 | 0 | 0 | 0
30 | [21 empty] | 0 | 0 | 0 | 0 | 0% | 0 | 1 | 0 | 0 | 0 | No | 0% | 0% | 1 | 1 | 1 | 0 |  |  | 0.15 | 0 | 0 | 0
31 | [21 empty] | 0 | 0 | 0 | 0 | 0% | 0 | 1 | 0 | 0 | 0 | No | 0% | 0% | 1 | 1 | 1 | 0 |  |  | 0.15 | 0 | 0 | 0
32 | [21 empty] | 0 | 0 | 0 | 0 | 0% | 0 | 1 | 0 | 0 | 0 | No | 0% | 0% | 1 | 1 | 1 | 0 |  |  | 0.15 | 0 | 0 | 0
33 | [21 empty] | 0 | 0 | 0 | 0 | 0% | 0 | 1 | 0 | 0 | 0 | No | 0% | 0% | 1 | 1 | 1 | 0 |  |  | 0.15 | 0 | 0 | 0
34 | [21 empty] | 0 | 0 | 0 | 0 | 0% | 0 | 1 | 0 | 0 | 0 | No | 0% | 0% | 1 | 1 | 1 | 0 |  |  | 0.15 | 0 | 0 | 0
35 | [21 empty] | 0 | 0 | 0 | 0 | 0% | 0 | 1 | 0 | 0 | 0 | No | 0% | 0% | 1 | 1 | 1 | 0 |  |  | 0.15 | 0 | 0 | 0
36 | [21 empty] | 0 | 0 | 0 | 0 | 0% | 0 | 1 | 0 | 0 | 0 | No | 0% | 0% | 1 | 1 | 1 | 0 |  |  | 0.15 | 0 | 0 | 0
37 | [21 empty] | 0 | 0 | 0 | 0 | 0% | 0 | 1 | 0 | 0 | 0 | No | 0% | 0% | 1 | 1 | 1 | 0 |  |  | 0.15 | 0 | 0 | 0
38 | [21 empty] | 0 | 0 | 0 | 0 | 0% | 0 | 1 | 0 | 0 | 0 | No | 0% | 0% | 1 | 1 | 1 | 0 |  |  | 0.15 | 0 | 0 | 0
Note on G6: Operating hours must be estimated using one of the six lighting schedules found in the Operating Schedules tab.

## Old op hr tables (hidden)
Operating Hour Schedules, User-Defined
Schedules used in Project Input table |  |  |  | Lighting run-time adjustment | Annual Occupancy Schedule |  |  | Weekday Occupancy Schedule |  |  | Weekend Occupancy Schedule
Operating Sched | Operating Hrs | Op Hrs-Calculated | Occupied Hours | On-time Factor | Weeks | Weekends | Shutdowns&Holidays | Begins | Ends | # days | Begins | Ends | # days
Schedule A | 52 | 52 | 52 | 100% | 1 | 1 | 0 | 8:00 | 18:00 | 5 | 9:00 | 11:00 | 1
Schedule B | 2422 | 2422 | 2422 | 100% | 52 | 52 | 14 | 8:00 | 17:00 | 5 | 8:00 | 12:00 | 1
Schedule C | 1900 | 1900 | 1900 | 100% | 42 | 0 | 20 | 7:00 | 17:00 | 5 |  |  | 0
Schedule D | 3660 | 3660 | 3660 | 100% | 52 | 52 | 7 | 6:00 | 18:00 | 5 | 8:00 | 14:00 | 2
Schedule E | 1005 | 1005 | 1005 | 100% | 52 | 0 | 7 | 12:00 | 17:00 | 4 |  |  | 0
Schedule F | 2996.7 | 2996.7 | 2854 | 105% | 52 | 52 | 10 | 7:00 | 18:00 | 5 | 9:00 | 11:00 | 1
Schedule G | 6 | 6 | 6 | 100% | 1 | 0 | 0 | 22:00 | 4:00 | 1 | 9:00 | 11:00 | 0
Schedule H | 8760
Schedule I | 0
Schedule J | 0
Note: Following are acceptable formats for entering time in above table:
[8 empty] | Entering: | 8: | results in 8:00 AM
[8 empty] | Entering: | 2 pm | results in 2:00 PM
[8 empty] | Entering: | 15:30 | results in 3:30 PM
Operating hour worksheet-for use in estimating operating hours for spaces with multiple occupancy schedules
SPACE TYPE 1
Schedule | Mon | Tues | Wed | Thurs | Fri | Sat | Su |  |  |  | Note: total operating hours can be manually transferred to the above user input table (Schedules H,I,or J) for use in calculations
Name | 1 | 2 | 3 | 4 | 5 | 6 | 7 | Hrs/week | Weeks/yr | Hrs/yr
Schedule 1 | 9 | 9 | 9 | 9 | 9 | 3 | 0 | 48 | 48 | 2304
Schedule 2 | 0 | 9 | 9 | 9 | 9 | 0 | 0 | 36 | 4 | 144
Schedule 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Schedule 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Schedule 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Holiday | 14 | days/yr |  | 0 | hrs/holiday occupied |  |  |  | Holiday adj: | -126
[9 empty] | Total operating hours | 2322
Note: Holiday adjustment factor uses the first non-zero value in Schedule 1 to estimate holiday unoccupied hours.
SPACE TYPE 2
Schedule | Mon | Tues | Wed | Thurs | Fri | Sat | Su
Name | 1 | 2 | 3 | 4 | 5 | 6 | 7 | Hrs/week | Weeks/yr | Hrs/yr
Schedule 1 | 8 | 8 | 8 | 8 | 8 | 0 | 0 | 40 | 42 | 1680
Schedule 2 | 6 | 6 | 6 | 6 | 0 | 0 | 0 | 24 | 2 | 48
Schedule 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0
Schedule 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Schedule 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Holiday | 10 | days/yr |  | 0 | hrs/holiday occupied |  |  |  | Holiday adj: | -80
[9 empty] | Total operating hours | 1648
SPACE TYPE 3
Schedule | Mon | Tues | Wed | Thurs | Fri | Sat | Su
Name | 1 | 2 | 3 | 4 | 5 | 6 | 7 | Hrs/week | Weeks/yr | Hrs/yr
Schedule 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0
Schedule 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Schedule 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Schedule 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Schedule 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Holiday | 0 | days/yr |  | 0 | hrs/holiday occupied |  |  |  | Holiday adj: | 0
[9 empty] | Total operating hours | 0
SPACE TYPE 4
Schedule | Mon | Tues | Wed | Thurs | Fri | Sat | Su
Name | 1 | 2 | 3 | 4 | 5 | 6 | 7 | Hrs/week | Weeks/yr | Hrs/yr
Schedule 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0
Schedule 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0
Schedule 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Schedule 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Schedule 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Holiday | 0 | days/yr |  | 0 | hrs/holiday occupied |  |  |  | Holiday adj: | 0
[9 empty] | Total operating hours | 0
Instructions:
To estimate lighting operating hours based on building operating (or occupancy) hours, enter the typical weekly operating schedules in the below table, then select the appropriate operating schedule in the Project Input Table. Lighting run-time can be adjusted by the run-time adjustment factor to account for actual operating conditions (e.g., lights are turned off one hour before and one hour after the space is occupied).

## Operating Schedules
Enter up to six (6) light schedules to define the annual lighting operating hours for the facility | [17 empty] | scroll right to input additional schedules
Operating Schedule |  | Light Schedule #1 |  |  | Annual run-time (hrs) | 2085.7143 | Light Schedule #2 |  |  | Annual run-time (hrs) | 3842.8571 | Light Schedule #3 |  |  | Annual run-time (hrs) | 4171.4286 | Light Schedule #4 |  |  | Annual run-time (hrs) | 2507.1429 | Light Schedule #5 |  |  | Annual run-time (hrs) | 2311.6071 | Light Schedule #6 |  |  | Annual run-time (hrs) | 1717.2024 | Operating Schedules
Schedule #1 | 2085.7143 | Does the light schedule vary during different times of the year? |  |  |  |  | Does the light schedule vary during different times of the year? |  |  |  |  | Does the light schedule vary during different times of the year? |  |  |  |  | Does the light schedule vary during different times of the year? |  |  |  |  | Does the light schedule vary during different times of the year? |  |  |  |  | Does the light schedule vary during different times of the year? |  |  |  |  | Sched #1 (2,086 hrs) | Sched #4 (2,507 hrs)
Schedule #2 | 3842.8571 | No | If yes, up to 3 seasonal sched. may be entered |  |  |  | No | If yes, up to 3 seasonal sched. may be entered |  |  |  | No | If yes, up to 3 seasonal sched. may be entered |  |  |  | No | If yes, up to 3 seasonal sched. may be entered |  |  |  | Yes | If yes, up to 3 seasonal sched. may be entered |  |  |  | Yes | If yes, up to 3 seasonal sched. may be entered |  |  |  | Sched #2 (3,843 hrs) | Sched #5 (2,312 hrs)
Schedule #3 | 4171.4286 | 1 | Enter the number of seasonal schedules |  |  |  | 2 | Enter the number of seasonal schedules |  |  |  | 2 | Enter the number of seasonal schedules |  |  |  | 2 | Enter the number of seasonal schedules |  |  |  | 2 | Enter the number of seasonal schedules |  |  |  | 3 | Enter the number of seasonal schedules |  |  |  | Sched #3 (4,171 hrs) | Sched #6 (1,717 hrs)
Schedule #4 | 2507.1429 | Annual Schedule |  |  |  |  | Annual Schedule |  |  |  |  | Annual Schedule |  |  |  |  | Annual Schedule |  |  |  |  | Season #1 |  |  |  |  | Season #1
Schedule #5 | 2311.6071 | # of Months | 12 |  |  |  | # of Months | 12 |  |  |  | # of Months | 12 |  |  |  | # of Months | 12 |  |  |  | # of Months | 10 |  |  |  | # of Months | 7
Schedule #6 | 1717.2024 | Warning: the number of months entered exceeds 12 |  |  |  |  | Warning: the number of months entered exceeds 12 |  |  |  |  | Warning: the number of months entered exceeds 12 |  |  |  |  | Warning: the number of months entered exceeds 12 |  |  |  |  | Warning: the number of months entered exceeds 12 |  |  |  |  | Warning: the number of months entered exceeds 12
|  | Weekly Schedule |  |  |  |  | Weekly Schedule |  |  |  |  | Weekly Schedule |  |  |  |  | Weekly Schedule |  |  |  |  | Weekly Schedule |  |  |  |  | Weekly Schedule
|  | Is Mon - Fri schedule the same? |  |  | Yes |  | Is Mon - Fri schedule the same? |  |  | No |  | Is Mon - Fri schedule the same? |  |  | Yes |  | Is Mon - Fri schedule the same? |  |  | Yes |  | Is Mon - Fri schedule the same? |  |  | No |  | Is Mon - Fri schedule the same? |  |  | Yes
|  |  | Time On | Time Off |  |  |  | Time On | Time Off |  |  |  | Time On | Time Off |  |  |  | Time On | Time Off |  |  |  | Time On | Time Off |  |  |  | Time On | Time Off
|  | Mon-Fri | 9:00 | 17:00 |  |  | Mon | 18:00 | 6:00 |  |  | Mon-Fri | 6:00 | 22:00 |  |  | Mon-Fri | 7:00 | 17:00 |  |  | Mon | 7:00 | 17:00 |  |  | Mon-Fri | 7:00 | 17:00
|  | Tue |  |  |  |  | Tue | 7:00 | 17:00 |  |  | Tue | 7:00 | 17:00 |  |  | Tue | 7:00 | 17:00 |  |  | Tue | 7:00 | 17:00 |  |  | Tue | 7:00 | 17:00
|  | Wed |  |  |  |  | Wed | 7:00 | 17:00 |  |  | Wed | 7:00 | 17:00 |  |  | Wed | 7:00 | 17:00 |  |  | Wed | 7:00 | 17:00 |  |  | Wed | 7:00 | 17:00
|  | Thu |  |  |  |  | Thu | 7:00 | 17:00 |  |  | Thu | 7:00 | 17:00 |  |  | Thu | 7:00 | 17:00 |  |  | Thu | 7:00 | 17:00 |  |  | Thu | 7:00 | 17:00
|  | Fri |  |  |  |  | Fri | 7:00 | 17:00 |  |  | Fri | 7:00 | 18:30 |  |  | Fri | 7:00 | 18:30 |  |  | Fri | 7:00 | 18:30 |  |  | Fri | 7:00 | 17:00
|  | Sat | Off |  |  |  | Sat | 18:00 | 6:00 |  |  | Sat | Off | 22:00 |  |  | Sat | Off | 22:00 |  |  | Sat | 8:00 | 12:00 |  |  | Sat | Off | 22:00
|  | Sun | Off |  |  |  | Sun | 18:00 | 6:00 |  |  | Sun | Off | 23:00 |  |  | Sun | Off | 23:00 |  |  | Sun | Off | 23:00 |  |  | Sun | Off | 23:00
|  | # of Holidays | 0 |  |  |  | # of Holidays | 10 |  |  |  | # of Holidays |  |  |  |  | # of Holidays | 10 |  |  |  | # of Holidays | 10 |  |  |  | # of Holidays | 6
|  | Note: lights are assumed off during holidays. Entering holidays reduces the annual operating hours |  |  |  |  | Note: lights are assumed off during holidays. Entering holidays reduces the annual operating hours |  |  |  |  | Note: lights are assumed off during holidays. Entering holidays reduces the annual operating hours |  |  |  |  | Note: lights are assumed off during holidays. Entering holidays reduces the annual operating hours |  |  |  |  | Note: lights are assumed off during holidays. Entering holidays reduces the annual operating hours |  |  |  |  | Note: lights are assumed off during holidays. Entering holidays reduces the annual operating hours
|  | Season #2 |  |  |  |  | Season #2 |  |  |  |  | Season #2 |  |  |  |  | Season #2 |  |  |  |  | Season #2 |  |  |  |  | Season #2
|  | # of Months |  |  |  |  | # of Months |  |  |  |  | # of Months |  |  |  |  | # of Months |  |  |  |  | # of Months | 2 |  |  |  | # of Months | 3
|  | Weekly Schedule |  |  |  |  | Weekly Schedule |  |  |  |  | Weekly Schedule |  |  |  |  | Weekly Schedule |  |  |  |  | Weekly Schedule |  |  |  |  | Weekly Schedule
|  | Is Mon - Fri schedule the same? |  |  | No |  | Is Mon - Fri schedule the same? |  |  | No |  | Is Mon - Fri schedule the same? |  |  | No |  | Is Mon - Fri schedule the same? |  |  | Yes |  | Is Mon - Fri schedule the same? |  |  | No |  | Is Mon - Fri schedule the same? |  |  | No
|  |  | Time On | Time Off |  |  |  | Time On | Time Off |  |  |  | Time On | Time Off |  |  |  | Time On | Time Off |  |  |  | Time On | Time Off |  |  |  | Time On | Time Off
|  | Mon | 0:00 |  |  |  | Mon | Off |  |  |  | Mon | Off |  |  |  | Mon-Fri | Off |  |  |  | Mon | Off | 10:00 |  |  | Mon | 7:00 | 10:00
|  | Tue | Off |  |  |  | Tue | Off |  |  |  | Tue | Off | 0:15 |  |  | Tue | Off |  |  |  | Tue | Off |  |  |  | Tue | Off
|  | Wed | Off |  |  |  | Wed | Off |  |  |  | Wed | Off |  |  |  | Wed | Off |  |  |  | Wed | Off |  |  |  | Wed | Off
|  | Thu | Off |  |  |  | Thu | Off |  |  |  | Thu | Off |  |  |  | Thu | Off |  |  |  | Thu | Off |  |  |  | Thu | Off
|  | Fri | Off |  |  |  | Fri | Off |  |  |  | Fri | Off |  |  |  | Fri | Off |  |  |  | Fri | Off |  |  |  | Fri | Off
|  | Sat | Off |  |  |  | Sat | Off |  |  |  | Sat | Off |  |  |  | Sat | Off |  |  |  | Sat | Off |  |  |  | Sat | Off
|  | Sun | Off |  |  |  | Sun | Off |  |  |  | Sun | Off |  |  |  | Sun | Off |  |  |  | Sun | Off |  |  |  | Sun | Off
|  | # of Holidays | 0 |  |  |  | # of Holidays | 0 |  |  |  | # of Holidays | 0 |  |  |  | # of Holidays | 0 |  |  |  | # of Holidays | 0 |  |  |  | # of Holidays | 0
|  | Season #3 |  |  |  |  | Season #3 |  |  |  |  | Season #3 |  |  |  |  | Season #3 |  |  |  |  | Season #3 |  |  |  |  | Season #3
|  | # of Months |  |  |  |  | # of Months |  |  |  |  | # of Months |  |  |  |  | # of Months |  |  |  |  | # of Months |  |  |  |  | # of Months | 2
|  | Weekly Schedule |  |  |  |  | Weekly Schedule |  |  |  |  | Weekly Schedule |  |  |  |  | Weekly Schedule |  |  |  |  | Weekly Schedule |  |  |  |  | Weekly Schedule
|  | Is Mon - Fri schedule the same? |  |  | No |  | Is Mon - Fri schedule the same? |  |  | No |  | Is Mon - Fri schedule the same? |  |  | No |  | Is Mon - Fri schedule the same? |  |  | No |  | Is Mon - Fri schedule the same? |  |  | No |  | Is Mon - Fri schedule the same? |  |  | Yes
|  |  | Time On | Time Off |  |  |  | Time On | Time Off |  |  |  | Time On | Time Off |  |  |  | Time On | Time Off |  |  |  | Time On | Time Off |  |  |  | Time On | Time Off
|  | Mon | Off |  |  |  | Mon | Off |  |  |  | Mon | Off |  |  |  | Mon | Off |  |  |  | Mon | Off |  |  |  | Mon-Fri | 12:00 | 17:00
|  | Tue | Off |  |  |  | Tue | Off | 0:00 |  |  | Tue | Off |  |  |  | Tue | Off |  |  |  | Tue | Off |  |  |  | Tue | Off | 0:15
|  | Wed | Off |  |  |  | Wed | Off | 0:30 |  |  | Wed | Off |  |  |  | Wed | Off |  |  |  | Wed | Off | 0:15 |  |  | Wed | Off
|  | Thu | Off |  |  |  | Thu | Off |  |  |  | Thu | Off |  |  |  | Thu | Off |  |  |  | Thu | Off |  |  |  | Thu | Off
|  | Fri | Off |  |  |  | Fri | Off |  |  |  | Fri | Off |  |  |  | Fri | Off |  |  |  | Fri | Off |  |  |  | Fri | Off
|  | Sat | Off |  |  |  | Sat | Off |  |  |  | Sat | Off |  |  |  | Sat | Off |  |  |  | Sat | Off |  |  |  | Sat | Off
|  | Sun | Off |  |  |  | Sun | Off | 1:00 |  |  | Sun | Off |  |  |  | Sun | Off |  |  |  | Sun | Off |  |  |  | Sun | Off
|  | # of Holidays | 0 |  |  |  | # of Holidays | 0 |  |  |  | # of Holidays | 0 |  |  |  | # of Holidays | 0 |  |  |  | # of Holidays | 0 |  |  |  | # of Holidays | 0
|  | Sum of entered months - if greater than 12, months are automatically reduced in op hr calculation |  |  |  |  | Sum of entered months - if greater than 12, months are automatically reduced in op hr calculation |  |  |  |  | Sum of entered months - if greater than 12, months are automatically reduced in op hr calculation |  |  |  |  | Sum of entered months - if greater than 12, months are automatically reduced in op hr calculation |  |  |  |  | Sum of entered months - if greater than 12, months are automatically reduced in op hr calculation |  |  |  |  | Sum of entered months - if greater than 12, months are automatically reduced in op hr calculation
|  | 12 |  |  |  |  | 12 |  |  |  |  | 12 |  |  |  |  | 12 |  |  |  |  | 12 |  |  |  |  | 12
|  | Seasonal months |  |  |  |  | Seasonal months |  |  |  |  | Seasonal months |  |  |  |  | Seasonal months |  |  |  |  | Seasonal months |  |  |  |  | Seasonal months
|  | 12 | 0 | 0 |  |  | 12 | 0 | 0 |  |  | 12 | 0 | 0 |  |  | 12 | 0 | 0 |  |  | 10 | 2 | 0 |  |  | 7 | 3 | 2
|  | seasonal months adjusted if sum exceeds 12 |  |  |  |  | seasonal months adjusted if sum exceeds 12 |  |  |  |  | seasonal months adjusted if sum exceeds 12 |  |  |  |  | seasonal months adjusted if sum exceeds 12 |  |  |  |  | seasonal months adjusted if sum exceeds 12 |  |  |  |  | seasonal months adjusted if sum exceeds 12
|  | protects from overestimating savings due to dynamic lookup function error |  |  |  |  | protects from overestimating savings due to dynamic lookup function error |  |  |  |  | protects from overestimating savings due to dynamic lookup function error |  |  |  |  | protects from overestimating savings due to dynamic lookup function error |  |  |  |  | protects from overestimating savings due to dynamic lookup function error |  |  |  |  | protects from overestimating savings due to dynamic lookup function error
|  | Calculated daily op hrs |  |  |  |  | Calculated daily op hrs |  |  |  |  | Calculated daily op hrs |  |  |  |  | Calculated daily op hrs |  |  |  |  | Calculated daily op hrs |  |  |  |  | Calculated daily op hrs
|  | seas1 hrs | seas 2 hrs | seas3 hrs |  |  | seas1 hrs | seas 2 hrs | seas3 hrs |  |  | seas1 hrs | seas 2 hrs | seas3 hrs |  |  | seas1 hrs | seas 2 hrs | seas3 hrs |  |  | seas1 hrs | seas 2 hrs | seas3 hrs |  |  | seas1 hrs | seas 2 hrs | seas3 hrs
|  | 8 | 0 | 0 |  |  | 12 | 0 | 0 |  |  | 16 | 0 | 0 |  |  | 10 | 0 | 0 |  |  | 10 | 0 | 0 |  |  | 10 | 3 | 5
|  | 8 | 0 | 0 |  |  | 10 | 0 | 0 |  |  | 16 | 0 | 0 |  |  | 10 | 0 | 0 |  |  | 10 | 0 | 0 |  |  | 10 | 0 | 5
|  | 8 | 0 | 0 |  |  | 10 | 0 | 0 |  |  | 16 | 0 | 0 |  |  | 10 | 0 | 0 |  |  | 10 | 0 | 0 |  |  | 10 | 0 | 5
|  | 8 | 0 | 0 |  |  | 10 | 0 | 0 |  |  | 16 | 0 | 0 |  |  | 10 | 0 | 0 |  |  | 10 | 0 | 0 |  |  | 10 | 0 | 5
|  | 8 | 0 | 0 |  |  | 10 | 0 | 0 |  |  | 16 | 0 | 0 |  |  | 10 | 0 | 0 |  |  | 11.5 | 0 | 0 |  |  | 10 | 0 | 5
|  | 0 | 0 | 0 |  |  | 12 | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 4 | 0 | 0 |  |  | 0 | 0 | 0
|  | 0 | 0 | 0 |  |  | 12 | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 0 |  |  | 0 | 0 | 0
|  | Weekly hrs |  |  |  |  | Weekly hrs |  |  |  |  | Weekly hrs |  |  |  |  | Weekly hrs |  |  |  |  | Weekly hrs |  |  |  |  | Weekly hrs
|  | 40 | 0 | 0 |  |  | 76 | 0 | 0 |  |  | 80 | 0 | 0 |  |  | 50 | 0 | 0 |  |  | 55.5 | 0 | 0 |  |  | 50 | 3 | 25
|  | Annual hrs |  |  |  |  | Annual hrs |  |  |  |  | Annual hrs |  |  |  |  | Annual hrs |  |  |  |  | Annual hrs |  |  |  |  | Annual hrs
|  | 2085.7143 | 0 | 0 |  |  | 3842.8571 | 0 | 0 |  |  | 4171.4286 | 0 | 0 |  |  | 2507.1429 | 0 | 0 |  |  | 2311.6071 | 0 | 0 |  |  | 1460.8333 | 39.1071 | 217.2619
|  | Sum of annual hours - controlled by # of seasons entry. |  |  |  |  | Sum of annual hours - controlled by # of seasons entry. |  |  |  |  | Sum of annual hours - controlled by # of seasons entry. |  |  |  |  | Sum of annual hours - controlled by # of seasons entry. |  |  |  |  | Sum of annual hours - controlled by # of seasons entry. |  |  |  |  | Sum of annual hours - controlled by # of seasons entry.
|  | 2085.7143 |  |  |  |  | 3842.8571 |  |  |  |  | 4171.4286 |  |  |  |  | 2507.1429 |  |  |  |  | 2311.6071 |  |  |  |  | 1717.2024
|  | Dynamic range for season2&3 lookup values |  |  |  |  | Dynamic range for season2&3 lookup values |  |  |  |  | Dynamic range for season2&3 lookup values |  |  |  |  | Dynamic range for season2&3 lookup values |  |  |  |  | Dynamic range for season2&3 lookup values |  |  |  |  | Dynamic range for season2&3 lookup values
|  | 0 |  |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
|  | 1 |  |  |  |  | 1 |  |  |  |  | 1 |  |  |  |  | 1 |  |  |  |  | 1 |  |  |  |  | 1
|  | 2 |  |  |  |  | 2 |  |  |  |  | 2 |  |  |  |  | 2 |  |  |  |  | 2 |  |  |  |  | 2
|  | 3 |  |  |  |  | 3 |  |  |  |  | 3 |  |  |  |  | 3 |  |  |  |  | 3 |  |  |  |  | 3
|  | 4 |  |  |  |  | 4 |  |  |  |  | 4 |  |  |  |  | 4 |  |  |  |  | 4 |  |  |  |  | 4
|  | 5 |  |  |  |  | 5 |  |  |  |  | 5 |  |  |  |  | 5 |  |  |  |  | 5 |  |  |  |  | 5
|  | 6 |  |  |  |  | 6 |  |  |  |  | 6 |  |  |  |  | 6 |  |  |  |  | 6 |  |  |  |  | 6
|  | 7 |  |  |  |  | 7 |  |  |  |  | 7 |  |  |  |  | 7 |  |  |  |  | 7 |  |  |  |  | 7
|  | 8 |  |  |  |  | 8 |  |  |  |  | 8 |  |  |  |  | 8 |  |  |  |  | 8 |  |  |  |  | 8
|  | 9 |  |  |  |  | 9 |  |  |  |  | 9 |  |  |  |  | 9 |  |  |  |  | 9 |  |  |  |  | 9
|  | 10 |  |  |  |  | 10 |  |  |  |  | 10 |  |  |  |  | 10 |  |  |  |  | 10 |  |  |  |  | 10
|  | 11 |  |  |  |  | 11 |  |  |  |  | 11 |  |  |  |  | 11 |  |  |  |  | 11 |  |  |  |  | 11
|  | 12 |  |  |  |  | 12 |  |  |  |  | 12 |  |  |  |  | 12 |  |  |  |  | 12 |  |  |  |  | 12
|  | Offset |  |  |  |  | Offset |  |  |  |  | Offset |  |  |  |  | Offset |  |  |  |  | Offset |  |  |  |  | Offset
|  | 1 | Offset for defining season 2 range |  |  |  | 1 | Offset for defining season 2 range |  |  |  | 1 | Offset for defining season 2 range |  |  |  | 1 | Offset for defining season 2 range |  |  |  | 3 | Offset for defining season 2 range |  |  |  | 6 | Offset for defining season 2 range
|  | 1 | Offset for defining season 3 range |  |  |  | 1 | Offset for defining season 3 range |  |  |  | 1 | Offset for defining season 3 range |  |  |  | 1 | Offset for defining season 3 range |  |  |  | 1 | Offset for defining season 3 range |  |  |  | 3 | Offset for defining season 3 range

## Project Summary Report
Project Name | 0
Climate Zone | CZ03
KWh Savings | 0
Peak kW Reduction | 0 | [13 empty] | Optional
% Savings | #DIV/0!
Rebate Amount | 0
|  |  | Pre-existing light fixtures |  | Lighting measure description |  |  | Savings summary |  | Key parameters
Space Description | Space end use type | Space ID | Qty | Lamp Description | Meas Qty | Measure Lamp Description | New Control Type | kWh Savings | Peak kW Re-duction | Control Savings | User-Defined Control Savings? | Op Hrs | Op Hrs - Default or User Input? | Rebate Amount | Negative Therms Impact
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% |  | 0 |  | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% |  | 0 |  | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% |  | 0 |  | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% |  | 0 |  | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% |  | 0 |  | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% |  | 0 |  | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% |  | 0 |  | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% |  | 0 |  | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% |  | 0 |  | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% |  | 0 |  | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% |  | 0 |  | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% |  | 0 |  | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% |  | 0 |  | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% |  | 0 |  | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% |  | 0 |  | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% |  | 0 |  | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% |  | 0 |  | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% |  | 0 |  | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% |  | 0 |  | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% |  | 0 |  | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% |  | 0 |  | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% |  | 0 |  | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% |  | 0 |  | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% |  | 0 |  | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% |  | 0 |  | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% |  | 0 |  | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% |  | 0 |  | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% |  | 0 |  | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% |  | 0 |  | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% |  | 0 |  | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% |  | 0 |  | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% |  | 0 |  | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% |  | 0 |  | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% |  | 0 |  | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% |  | 0 |  | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% |  | 0 |  | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% |  | 0 |  | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% |  | 0 |  | 0 | 0
Total |  |  | 0 |  | 0 |  |  | 0 | 0 |  |  |  |  | 0 | 0

## T24 Analysis-Replacement (hidden)
Lighting Fixture Replacements (Lighting Alterations)
Interior fixture replacements are generally classified as lighting alterations in the 2013 Title 24 Building Energy Efficiency Standards (Section 141-Alterations)
The following table is used to identify the most common conditions that invoke code compliance for a lighting fixture replacement. If any of the conditions apply, then the lesser of the code baseline or the pre-existing power is used to estimate savings. To determine the full extent of Title 24 code compliance, see Title 24 Section 141 - Alterations.
Follow the instructions to complete the table. If Title 24 lighting power allowances (LPA) apply, the savings estimate baseline power for each measure assigned to the space will be adjusted if the code allowance (watts/sf) is less than the existing lighting power density (LPD, watts per sf). If the space is subject to mandatory occupancy sensor controls, the occupancy sensor savings factor is applied to the baseline energy use.
Title 24 regulations evaluated in table: |  | 2013
Space ID | Space Description | Space use type | Area (sq ft) | 1) Will the space end-use type or floor area be changed as part of a remodel? | 2) Will 10% or more of the space fixtures be replaced? | 3) Other conditions are found to invoke code compliance. Use code baseline | Title 24 LPA applies? | Total (pre-existing) fixture count | Code LPA (w/sf) | Exist fixture w/sf | Existing kW | Baseline kW | kW adj factor | Are occupancy sensor controls mandatory? | Is efficient case lighting LPD > 85% of LPA?
A | [6 empty] | No | 0 |  |  | 0 | 0 | 1 | No
B | [6 empty] | No | 0 |  |  | 0 | 0 | 1 | No
C | [6 empty] | No | 0 |  |  | 0 | 0 | 1 | No
D | [6 empty] | No | 0 |  |  | 0 | 0 | 1 | No
E | [6 empty] | No | 0 |  |  | 0 | 0 | 1 | No
F | [6 empty] | No | 0 |  |  | 0 | 0 | 1 | No
G | [6 empty] | No | 0 |  |  | 0 | 0 | 1 | No
H | [6 empty] | No | 0 |  |  | 0 | 0 | 1 | No
I | [6 empty] | No | 0 |  |  | 0 | 0 | 1 | No
J | [6 empty] | No | 0 |  |  | 0 | 0 | 1 | No
K | [6 empty] | No | 0 |  |  | 0 | 0 | 1 | No
L | [6 empty] | No | 0 |  |  | 0 | 0 | 1 | No
0
Instructions
1 | Enter a space description and select a space use type - the space use type will determine the appropriate code LPA requirements.
2 | Enter the floor area of the space in square feet
3 | Answer each of the following questions and statements:
Question 1 | Will the space end-use type or floor area be changed as part of a remodel?
If yes, then Title 24 applies.
The space end use type refers to the functional use of the space (e.g., an office as compared to a warehouse) and not a change in tenant or ownership.
Question 2 | Will 10% or more of the space fixtures be replaced?
If yes, then Title 24 applies.
Space is defined as the space enclosed by four walls and/or partitions.
Statement | Other conditions are found to invoke code compliance. Use code baseline
Other conditions, such as branch circuit re-wiring, may invoke code compliance.
Enter "use code baseline" if other conditions identified in Title 24, Section 141 require the retrofit to meet code.
If Title 24 LPA applies to any of the spaces, return to the Project Input Table and assign each measure to the appropriate space.
To assign a measure to a space, select the measure type (replacement, retrofit, exterior) and space ID letter.
For measures assigned to a space, verify the space use type entered in the Project Input Table matches the space use type entered in the Title 24 table.
The following diagram illustrates the process for determining if a code baseline is used in the savings analysis.
Space Use Types covered by occupancy sensor control requirements (Section 130.1)
Classroom, whole bldg
Classrooms, lecture, vocational, training
Commercial and industrial refrigerated storage areas
Commercial and industrial storage areas
Commercial and industrial storage-whole bldg
Convention, conference, multipurpose, meeting centers
Corridors, restrooms, stairs, support areas
Exterior
Library, stacks
Office space < 250 sf
Office space, multipurpose <1,000 sf
Office space, conference room
Parking garage, parking area
Parking garage
Parking garage, whole bldg
Note on R10: Information only. Used to determine if compliance with Section 130.1D (daylighting) is required. If required, each space fixture within a daylit zone must be controlled by automatic daylighting controls.

## T24 Analysis-Retrofit (hidden)
Interior Lighting Fixture Retrofits (Lighting Modifications-in-Place)
Interior fixture retrofits are generally defined as lighting Modifications-in-Place by the Title 24 2013 Building Energy Efficiency Standards.
The following table is used to identify the most common conditions that invoke code compliance for a lighting retrofit. To determine the full extent of Title 24 code compliance, see Title 24 Section 141 - Alterations.
Follow the instructions to complete the table. If Title 24 lighting power allowance (LPA) applies, the baseline power for each measure assigned to the space will be adjusted if the lighting power allowance (watts per sf) is less than the existing lighting power density (LPD, watts per sf). If the space is subject to mandatory occupancy sensor controls, the occupancy sensor savings factor is applied to the baseline energy use.
Title 24 regulations evaluated in table: |  | 2013 | Note: prior to the 2013 version, Title 24 did not apply to fixture retrofits
Space ID | Space Description | Space use type | Area (sq ft) | 1) Will the fixtures be retrofitted as part of a general remodel? | 2) Will the space end-use type or floor area be changed? | 3) Will 10% or more of the fixtures in the space be retrofitted? | 4) Will 40 or more fixtures be retrofitted? | 5) Other conditions are found to invoke code compliance. Use code baseline | Title 24 LPA applies? | Total (pre-existing) fixture count | Code LPA (w/sf) | Exist fixture w/sf | Existing kW | Baseline kW | kW adj factor | Are occupancy sensor controls mandatory? | Is efficient case lighting LPD > 85% of LPA?
M | [8 empty] | No | 0 |  |  | 0 | 0 | 1 | No
N | [8 empty] | No | 0 |  |  | 0 | 0 | 1 | No
O | [8 empty] | No | 0 |  |  | 0 | 0 | 1 | No
P | [8 empty] | No | 0 |  |  | 0 | 0 | 1 | No
Q | [8 empty] | No | 0 |  |  | 0 | 0 | 1 | No
R | [8 empty] | No | 0 |  |  | 0 | 0 | 1 | No
S | [8 empty] | No | 0 |  |  | 0 | 0 | 1 | No
T | [8 empty] | No | 0 |  |  | 0 | 0 | 1 | No
U | [8 empty] | No | 0 |  |  | 0 | 0 | 1 | No
V | [8 empty] | No | 0 |  |  | 0 | 0 | 1 | No
W | [8 empty] | No | 0 |  |  | 0 | 0 | 1 | No
X | [8 empty] | No | 0 |  |  | 0 | 0 | 1 | No
0
Instructions
1 | Enter a space description and select a space use type - the use type will determine the appropriate code LPA requirements.
2 | Enter the floor area of the space in square feet
3 | Answer each of the following questions and statements:
Question 1 | Will the fixtures be retrofitted as part of a general remodel?
If yes, then the retrofit is considered a lighting alteration and is treated like a lighting replacement. For this scenario, the less than 40 fixture exemption no longer applies.
Question 2 | Will the space end-use type or floor area be changed?
If yes, then Title 24 applies.
Question 3 | Will 10% or more of the fixtures in the space be retrofitted?
If yes, then Title 24 applies
Question 4 | Will 40 or more fixtures be retrofitted?
If yes, then Title 24 applies. However, if the retrofit is part of a general remodel (question 1), then the exemption does not apply.
If less than 40 fixtures in a Building Space are modified in any one year, the modification is exempt from code . Building Space may be defined as either a single floor of a building, a tenant space, an enclosed space, or all of the common spaces on a single floor.
Statement | Other conditions are found to invoke code compliance. Use code baseline
Other conditions, such as branch circuit re-wiring, may invoke code compliance.
Enter "use code baseline" if other conditions identified in Title 24, Section 141 require the retrofit to meet code.
If Title 24 LPA applies to any of the spaces, return to the Project Input Table and assign each measure to the appropriate space.
To assign a measure to a space, select the measure type (replacement, retrofit, exterior) and space ID letter.
For measures assigned to a space, verify the space use type entered in the Project Input Table matches the space use type entered in the Title 24 table.
The following diagram illustrates the process for determining if a code baseline is used in the savings analysis.
Space Use Types covered by occupancy sensor control requirements (Section 130.1)
Classroom, whole bldg
Classrooms, lecture, vocational, training
Commercial and industrial refrigerated storage areas
Commercial and industrial storage areas
Commercial and industrial storage-whole bldg
Convention, conference, multipurpose, meeting centers
Corridors, restrooms, stairs, support areas
Exterior
Library, stacks
Office space < 250 sf
Office space, multipurpose <1,000 sf
Office space, conference room
Parking garage, parking area
Parking garage
Parking garage, whole bldg
Note on R10: Information only. Used to determine if compliance with Section 130.1D (daylighting) is required. If required, each space fixture within a daylit zone must be controlled by automatic daylighting controls.

## T24 Analysis-Exterior ltg (hidden)
Exterior Lighting Fixture Replacement
The following table is used to identify the most common conditions that invoke code compliance for an exterior lighting fixture replacement. To determine the full extent of Title 24 code compliance, see Title 24 Section 141 - Alterations.
Outdoor lighting is covered by Title 24 Standards, except for: temporary lighting, industrial sites, landscape, public streets & roadways, athletic fields, children's playground, FAA or coast guard regulated, ATMs, public monuments, theme parks, outdoor live performances or events, or historical buildings.
Exterior lighting is defined by lighting zones. Lighting zone 3 (urban areas) is the most common lighting zone.
Use the following table to determine if Title 24 lighting power allowances (LPA) or control requirements apply. If the space is subject to mandatory occupancy sensor controls, the measure baseline is adjusted by the motion sensor savings factor. If code LPA is applicable, follow Title 24 procedures to estimate the maximum lighting power allowed and enter the calculated total allowed power (watts) in the table. If the allowed power is less than pre-existing lighting power, the baseline power for each lighting measure assigned to the space will be adjusted.
Space ID | Description | Exterior Lighting Application | 1) Will 10% or more of the fixtures in the lighting application be replaced? | 2) Will 50% or more of the fixtures in the lighting application be replaced? | 3) Are the fixtures exempt from Title 24 motion sensor control requirements? | 3.1) If exempt, list exception to the code | Title 24 LPA applies? | 4) If LPA is applicable, enter the maximum allowed power in watts | Total (pre-existing) fixture count | Existing kW | Baseline kW | kW adj factor | Are motion sensor controls mandatory?
AA | [6 empty] | No |  | 0 | 0 | 0 | 1 | No
BB | [6 empty] | No |  | 0 | 0 | 0 | 1 | No
CC | [6 empty] | No |  | 0 | 0 | 0 | 1 | No
DD | [6 empty] | No |  | 0 | 0 | 0 | 1 | No
EE | [6 empty] | No |  | 0 | 0 | 0 | 1 | No
Instructions
1 | Enter a description and select the appropriate lighting application type.
2 | Answer each of the following questions:
Question 1 | Will 10% or more of the fixtures in the lighting application be replaced?
If yes, then Title 24 lighting control requirements apply.
Question 2 | Will 50% or more of the fixtures in the lighting application be replaced?
If yes, then Title 24 lighting power allowances (LPA) applies.
Question 3 | Are the fixtures exempt from Title 24 motion sensor control requirements?
There are numerous exceptions to the control requirements - if any are applicable, then the control requirements do not apply.
3.1 | If exempt, list the exception (e.g., fixtures are mounted higher than 24 ft above ground).
If LPA is applicable, enter the maximum allowed power in watts
If Title 24 lighting power allowances apply, follow Title 24 procedures for estimating the allowed power.
Enter the allowed power into the table using watts as the unit of measure.
If Title 24 LPA applies to any of the spaces, return to the Project Input Table and assign each measure to the appropriate space.
To assign a measure to a space, select the measure type (replacement, retrofit, exterior) and space ID letter.
| The following diagram illustrates the process for determining if a code baseline is used in the savings analysis. | [5 empty] | 2013 Title 24 Outdoor Lighting Power Allowances:

## Inventory Report
Pre-Existing Fixture Inventory
Project: | 0 | [5 empty] | Pre-Existing
Space Description | Space End Use Type | Lamp Description | Qty | Op Hrs | Control Type | Control Savings Factor | kW | kWh
0 | 0 | 0 | 0 |  | 0 | 0% | 0
0 | 0 | 0 | 0 |  | 0 | 0% | 0
0 | 0 | 0 | 0 |  | 0 | 0% | 0
0 | 0 | 0 | 0 |  | 0 | 0% | 0
0 | 0 | 0 | 0 |  | 0 | 0% | 0
0 | 0 | 0 | 0 |  | 0 | 0% | 0
0 | 0 | 0 | 0 |  | 0 | 0% | 0
0 | 0 | 0 | 0 |  | 0 | 0% | 0
0 | 0 | 0 | 0 |  | 0 | 0% | 0
0 | 0 | 0 | 0 |  | 0 | 0% | 0
0 | 0 | 0 | 0 |  | 0 | 0% | 0
0 | 0 | 0 | 0 |  | 0 | 0% | 0
0 | 0 | 0 | 0 |  | 0 | 0% | 0
0 | 0 | 0 | 0 |  | 0 | 0% | 0
0 | 0 | 0 | 0 |  | 0 | 0% | 0
0 | 0 | 0 | 0 |  | 0 | 0% | 0
0 | 0 | 0 | 0 |  | 0 | 0% | 0
0 | 0 | 0 | 0 |  | 0 | 0% | 0
0 | 0 | 0 | 0 |  | 0 | 0% | 0
0 | 0 | 0 | 0 |  | 0 | 0% | 0
0 | 0 | 0 | 0 |  | 0 | 0% | 0
0 | 0 | 0 | 0 |  | 0 | 0% | 0
0 | 0 | 0 | 0 |  | 0 | 0% | 0
0 | 0 | 0 | 0 |  | 0 | 0% | 0
0 | 0 | 0 | 0 |  | 0 | 0% | 0
0 | 0 | 0 | 0 |  | 0 | 0% | 0
0 | 0 | 0 | 0 |  | 0 | 0% | 0
0 | 0 | 0 | 0 |  | 0 | 0% | 0
0 | 0 | 0 | 0 |  | 0 | 0% | 0
0 | 0 | 0 | 0 |  | 0 | 0% | 0
0 | 0 | 0 | 0 |  | 0 | 0% | 0
0 | 0 | 0 | 0 |  | 0 | 0% | 0
0 | 0 | 0 | 0 |  | 0 | 0% | 0
0 | 0 | 0 | 0 |  | 0 | 0% | 0
0 | 0 | 0 | 0 |  | 0 | 0% | 0
0 | 0 | 0 | 0 |  | 0 | 0% | 0
0 | 0 | 0 | 0 |  | 0 | 0% | 0
0 | 0 | 0 | 0 |  | 0 | 0% | 0
Total |  |  | 0 |  |  |  | 0 | 0

## Energy savings methodology (hidden)
Energy savings methodology
The following describes the calculations used to estimate lighting energy savings:
Energy savings calculation section of the Project Input Table:
Energy Savings Calculation
kW pre-existing | KW code adj factor | kW baseline | kW efficient | operating hours | Mandatory OC or motion sensors? | baseline control adj factor | EC control % savings factor | HVAC IE Energy factor | HVAC IE Demand Factor | Coincident Demand Factor (CDF) | Efficient Fixture Qty
1.68 | 1 | 1.68 | 0.72 | 2420 | No | 6% | 34% | 1.09 | 1 | 0.02 | 15
kW pre-existing |  | Cell formula: | IF(ISNA(VLOOKUP(J7,INDIRECT(I7),2,FALSE)),0,IF(I7="User-defined",(D7*K7)/1000,IF(I7="",0,D7*VLOOKUP(J7,INDIRECT(I7),2,FALSE)/1000)))
The Fixture quantity is multiplied by either the user-defined fixture wattage or the default fixture wattage then divided by 1,000 to convert to kW
KW code adj factor |  | Cell formula: | IF(OR([@[Enter Space ID]]="",[@[Fixture Replacement or Fixture Retrofit]]=""),1,VLOOKUP([@[Enter Space ID]],INDIRECT(T7&"_table"),15,FALSE))
The kW adjustment factor is used to convert the pre-existing fixture kW to the code LPA fixture kW, if applicable. If not applicable, the adjustment factor is set to one.
kW baseline |  | Cell formula: | AA7*Z7
The pre-existing fixture kW is multiplied by the kW code adj factor to establish the baseline kW for the energy savings estimate.
kW efficient |  | Cell formula: | IF(ISNA(VLOOKUP(Q7,INDIRECT(P7),2,FALSE)),0,IF(P7="User-defined",(AL7*R7)/1000,IF(P7="",0,AL7*VLOOKUP(Q7,INDIRECT(P7),2,FALSE)/1000)))
The Efficient Fixture Qty is multiplied by either the user-defined efficient condition fixture wattage or the default efficient condition fixture wattage then divided by 1,000 to convert to kW
operating hours |  | Cell formula: | lookup formula
The operating hours are either the default operating hours obtained from the space use type table, or the Schedule operating hours estimated in the Op Hr Schedule Table
Mandatory OC or motion sensors? |  | Cell formula: | lookup formula
If the space the fixtures are assigned to in the Title 24 analysis indicates that: a) Title 24 applies, and b) the space type is subject to mandatory occupancy sensor controls, the answer is Yes. Otherwise, the answer is No.
baseline control adj factor |  | Cell formula: | lookup formula
If the fixtures are subject to mandatory occupancy sensor control, the occupancy control savings factor will be selected from the space use type table.
If not subject to code, and the existing control type selected is either occupancy sensor or manual bi-level switching, the control savings factor will be selected from the space use type table
EC control % savings factor |  | Cell formula: | lookup formula
If a occupancy sensor, daylight control, or a combination of the two are selected as the new control type, the appropriate control savings adjustment factor is selected from the space use type table
If user-defined savings is selected, then the percent savings factor entered in the table will be used.
HVAC IE Energy factor |  | Cell formula: | lookup formula
The interactive HVAC energy effects factor (for conditioned spaces) is determined by climate zone and is selected from the IE effects table.
The IE factor is used to adjust the baseline and efficient case energy use estimates to account for HVAC cooling savings associated with a reduction in lighting energy use.
HVAC IE Demand Factor |  | Cell formula: | lookup formula
The interactive HVAC demand effects factor (for conditioned spaces) is determined by climate zone and is selected from the IE effects table
The IE demand factor is used to adjust the peak demand reduction to account for HVAC cooling demand reductions associated with a reduction in lighting demand
Coincident Demand Factor (CDF) |  | Cell formula: | lookup formula
The coincident demand factor is determined by climate zone and is selected from the CDF table
The CDF factor accounts for the lighting demand reduction at the time of the electric system's peak demand
Efficient Fixture Qty |  | Cell formula: | lookup formula
The quantity of new lighting fixtures installed - may be different than the pre-existing fixture quantity
Energy savings summary section from the Project Input Table:
Energy Savings Summary
kWh baseline | kWh efficient | kWh savings | Peak kW reduction | % kWh Savings
34535.16 | 23333.9856 | 11201.1744 | 0.23793 | 32.43%
kWh baseline |  | Cell formula: | [@[kW baseline]]*[@[operating hours]]*[@[HVAC IE Energy factor]]*(1-[@[Pre-existing control adj factor]])
The baseline energy use is the baseline fixture kW multiplied by the operating hours, then adjusted for HVAC IE effects and the control savings factor
kWh efficient |  | Cell formula: | [@[kW efficient]]*[@[operating hours]]*[@[HVAC IE Energy factor]]*(1-IF([@[EC control % savings factor]]="NA",0,[@[EC control % savings factor]]))
The efficient condition energy use is the new fixture kW multiplied by the operating hours, then adjusted for HVAC IE effects and the new control savings factor
kWh savings |  | Cell formula: | [@[kWh baseline]]-[@[kWh efficient]]
The measure energy savings is the difference between baseline and new fixture energy use.
Peak kW reduction |  | Cell formula: | ([@[kW baseline]]-[@[kW efficient]])*[@[Coincident Demand Factor (CDF)]]*[@[HVAC IE Demand Factor]]
The electric system peak demand reduction is the difference between baseline and new fixture kW, multiplied by the coinidental demand factor and HVAC IE demand factor
% kWh Savings |  | Cell formula: | IF([@[kWh baseline]]=0,0,[@[kWh savings]]/[@[kWh baseline]])
Rebate calculation section from the Project Input Table (Optional)
Rebate Calculation
Incentive Level ($/kWh) | Rebate $
Incentive Level ($/kWh) |  | Cell formula: | No default formula - insert formula to retrieve one of two rebate levels listed in lookup tables tab (Rebate1 or Rebate2)
Rebate $ |  | Cell formula: | [@[Incentive Level ($/kWh)]]*[@[kWh savings]]
Natural gas interactive effects section from the Project Input Table
Nat. Gas IE
HVAC IE factor Therms/kWh | Therms
HVAC IE factor Therms/kWh |  | Cell formula: | IF(C7="",0,VLOOKUP(INDEX(space_use_type,MATCH(C7,space_type_list,0),2),Therms_table,MATCH($C$2,Therms_list,0),FALSE))
Look formula retrieves the climate zone specific HVAC interactive effects factor from the Therms-table located in the lookup tables tab (DEER 2011 default factors)
Therms |  | Cell formula: | [@[HVAC IE factor Therms/kWh]]*[@[kWh savings]]
Baseline fixture adjustment factor calculations from the T24 Analysis-Replacement Table:
Total (pre-existing) fixture count | Code LPA (w/sf) | Exist fixture w/sf | Existing kW | Baseline kW | kW adj factor | Are occupancy sensor controls mandatory? | Is efficient case lighting LPD > 85% of LPA?
10 | 0.9 | 1 | 10 | 9 | 0.9 | Yes | No
Total (pre-existing) fixture count |  | Cell formula: | lookup and sum array formula
Indicated the total quantity of fixtures assigned to a space from the Project Input Table
Code LPA (w/sf) |  | Cell formula: | IF($D11="","",IF($H11="Yes",VLOOKUP(C11,space_use_type,5,FALSE),""))
The lighting power density allowance is based on the space use type entered and is selected from the space use type table which contains T24 2013 lighting allowances
Exist fixture w/sf |  | Cell formula: | IF($D11="","",(L11*1000)/$D11)
The pre-existing fixture watts per square feet is calculated as the sum of pre-existing fixture wattage divided by the space area in square feet
Existing kW |  | Cell array formula: |  | {SUM((Input[Enter Space ID]='T24 Analysis Table'!$A10)*(Input[kW pre-existing]))}
The lighting fixture measures assigned to the space in the Project Input Table are summed to determined the space total fixture kW
Baseline kW |  | Cell formula: | IF(OR($J11<$K11,E11="Yes"),J11*$D11/1000,$L11)
The baseline kW is equal to the existing kW if T24 is not applicable.
If T24 is applicable, then the baseline kW is equal to the lesser of the existing kW or the code watts/sf multiplied by the space area and converted to kW
If the space use type has changed, then the code watts/sf is used to determine baseline kW
kW adj factor |  | Cell formula: | IF(OR($M11=0,L11=0),1,$M11/$L11)
The kW adjustment factor is the space baseline kW divided by the pre-existing kW. This factor is used in the Project Input Table
Are occupancy sensor controls mandatory? |  | Cell formula: | IF(H11="No","No",IF(ISNA(VLOOKUP(C11,OC_mandatory,1,FALSE)),"No","Yes"))
If Title 24 is applicable and the space use type is subject to mandatory occupancy sensor controls, the answer is Yes.
Is efficient case lighting LPD > 85% of LPA? |  | Cell array formula: |  | {IF(J11="","",IF(SUM((Input[Enter Space ID]='T24 Analysis-Replacement'!$A11)*(Input[kW efficient]))>(0.85*J11*D11/1000),"Yes","No"))}
If Title 24 is applicable and the total replacement fixture lighting power density (watts/sf) is greater than 85% of the lighting power allowance, then daylighting controls requirements apply to the space.
Only the space fixtures located in daylit zones are required to have daylighting controls. The savings calculations do not automatically account for daylighting. If daylit zone analysis indicates daylight controls
are required, the pre-existing controls should be set to daylight controls.
Baseline fixture adjustment factor calculations from the T24 Analysis-Retrofit Table:
Total (pre-existing) fixture count | Code LPA (w/sf) | Exist fixture w/sf | Existing kW | Baseline kW | kW adj factor | Are occupancy sensor controls mandatory? | Is efficient case lighting LPD > 85% of LPA?
10 | 0.9 | 1 | 10 | 9 | 0.9 | Yes | No
Total (pre-existing) fixture count |  | Cell formula: | lookup and sum array formula
Indicated the total quantity of fixtures assigned to a space from the Project Input Table
Code LPA (w/sf) |  | Cell formula: | IF($D11="","",IF($I11="Yes",VLOOKUP(C11,space_use_type,5,FALSE),""))
The lighting power density allowance is based on the space use type entered and is selected from the space use type table which contains T24 2013 lighting allowances
Exist fixture w/sf |  | Cell formula: | IF($D11="","",(M11*1000)/$D11)
The pre-existing fixture watts per square feet is calculated as the sum of pre-existing fixture wattage divided by the space area in square feet
Existing kW |  | Cell array formula: |  | {SUM((Input[Enter Space ID]='T24 Analysis Retrofit Table'!$A11)*(Input[kW pre-existing]))}
The lighting fixture measures assigned to the space in the Project Input Table are summed to determined the space total fixture kW
Baseline kW |  | Cell formula: | IF(OR($L11<$M11,F11="Yes"),$L11*$D11/1000,$N11)
The baseline kW is equal to the existing kW if T24 is not applicable.
If T24 is applicable, then the baseline kW is equal to the lesser of the existing kW or the code watts/sf multiplied by the space area and converted to kW
If the space use type has changed, then the code watts/sf is used to determine baseline kW
kW adj factor |  | Cell formula: | IF(OR($O11=0,N11=0),1,$O11/$N11)
The kW adjustment factor is the space baseline kW divided by the pre-existing kW. This factor is used in the Project Input Table
Are occupancy sensor controls mandatory? |  | Cell formula: | IF(J11="No","No",IF(ISNA(VLOOKUP(C11,OC_mandatory,1,FALSE)),"No","Yes"))
If Title 24 is applicable and the space use type is subject to mandatory occupancy sensor controls, the answer is Yes.
Is efficient case lighting LPD > 85% of LPA? |  | Cell array formula: |  | {IF(L11="","",IF(SUM((Input[Enter Space ID]=$A11)*(Input[kW efficient]))>(0.85*L11*D11/1000),"Yes","No"))}
If Title 24 is applicable and the total replacement fixture lighting power density (watts/sf) is greater than 85% of the lighting power allowance, then daylighting controls requirements apply to the space.
Only the space fixtures located in daylit zones are required to have daylighting controls. The savings calculations do not automatically account for daylighting. If daylit zone analysis indicates daylight controls
are required, the pre-existing controls should be set to daylight controls.
Baseline fixture adjustment factor calculations from the T24 Analysis-exterior lighting table:
Total (pre-existing) fixture count | Existing kW | Baseline kW | kW adj factor | Are motion sensor controls mandatory?
20 | 1.36 | 1.2 | 0.88235 | Yes
Total (pre-existing) fixture count |  | Cell formula: | lookup and sum array formula
Indicated the total quantity of fixtures assigned to a space from the Project Input Table
Existing kW |  | Cell array formula: |  | {SUM((Input[Enter Space ID]='T24 Analysis-Exterior ltg'!$A13)*(Input[kW pre-existing]))}
The lighting fixture measures assigned to the space in the Project Input Table are summed to determined the space total fixture kW
kW adj factor |  | Cell formula: | IF(AND(H13="Yes",(I13/1000)<K13),I13/1000,K13)
The kW adjustment factor is the space baseline kW divided by the pre-existing kW. This factor is used in the Project Input Table
Are motion sensor controls mandatory? |  | Cell formula: | IF(F13="Yes","No",IF(D13="Yes","Yes","No"))
If the lighting application is subject to mandatory occupancy sensor control, the answer is Yes.
𝑘𝑊𝑒𝑥𝑖𝑠𝑡 =𝑄 𝑥 𝑤𝑎𝑡𝑡𝑠/1000
𝑘𝑊𝑏𝑎𝑠𝑒𝑙𝑖𝑛𝑒=𝑘𝑊𝑒𝑥𝑖𝑠𝑡 𝑥 𝑘𝑊𝑎𝑑𝑗
𝑘𝑊𝑒𝑐 =𝑄𝑒𝑐 𝑥 𝑤𝑎𝑡𝑡𝑠/1000
𝑘𝑊ℎ 𝑏𝑎𝑠𝑒=𝑘𝑊𝑏𝑎𝑠𝑒×𝑂𝐻 ×𝐼𝐸𝑒𝑛𝑒𝑟𝑔𝑦 ×(1−𝐶𝐹𝑝𝑟𝑒𝑒𝑥𝑖𝑠𝑡)
𝑘𝑊ℎ 𝑒𝑐=𝑘𝑊𝑒𝑐×𝑂𝐻 ×𝐼𝐸𝑒𝑛𝑒𝑟𝑔𝑦 ×(1−𝐶𝐹𝑒𝑐)
𝑘𝑊ℎ 𝑠𝑎𝑣𝑖𝑛𝑔𝑠=𝑘𝑊ℎ 𝑏𝑎𝑠𝑒 −𝑘𝑊ℎ 𝑒𝑐
𝑘𝑊𝑝𝑘 =(𝑘𝑊𝑏𝑎𝑠𝑒 −𝑘𝑊𝑒𝑐)×𝐶𝐷𝐹 ×𝐼𝐸𝑑𝑒𝑚𝑎𝑛𝑑
𝑘𝑊ℎ 𝑠𝑎𝑣𝑖𝑛𝑔𝑠, % = (𝑘𝑊ℎ 𝑠𝑎𝑣𝑖𝑛𝑔𝑠)/(𝑘𝑊ℎ 𝑏𝑎𝑠𝑒𝑙𝑖𝑛𝑒)
watts/sf = (𝑘𝑊𝑒𝑥𝑖𝑠𝑡 ×1000)/𝐴
𝑘𝑊𝑏𝑎𝑠𝑒=𝑘𝑊𝑒𝑥𝑖𝑠𝑡 𝑜𝑟; ( 𝑤𝑎𝑡𝑡𝑠/𝑠𝑓 𝑐𝑜𝑑𝑒 ×𝐴 )/1000
𝑘𝑊𝑎𝑑𝑗=(𝑘𝑊𝑏𝑎𝑠𝑒 )/(𝑘𝑊 𝑒𝑥𝑖𝑠𝑡)
𝑇𝑜𝑡𝑎𝑙 𝑀𝑒𝑎𝑠𝑢𝑟𝑒 𝑅𝑒𝑏𝑎𝑡𝑒 ($)=𝑖𝑛𝑐𝑒𝑛𝑡𝑖𝑣𝑒 𝑟𝑎𝑡𝑒 × 𝑘𝑊ℎ 𝑠𝑎𝑣𝑖𝑛𝑔𝑠
𝑇ℎ𝑒𝑟𝑚𝑠 =𝐻𝑉𝐴𝐶 𝐼𝐸 𝑓𝑎𝑐𝑡𝑜𝑟 (𝑡ℎ𝑒𝑟𝑚𝑠/𝑘𝑊ℎ) × 𝑘𝑊ℎ 𝑠𝑎𝑣𝑖𝑛𝑔𝑠

## Early Retirement Reporting
Early Retirement Measures with Dual Baselines
Used for entering project savings into E3 reporting tool
Project Summary
ENTER total project cost (labor and materials)
Quantity | Rebate | Energy Savings (KWh) | Peak DR (kW) | EUL | RUL | Energy Savings, second baseline | Peak DR, second baseline | Participant cost, ER
0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | #DIV/0!
E3 Reporting Tool Inputs
Notes
1. In order for the early retirement (accelerated replacement) calculation to function in the custom measure section of the E3 reporting tool, four (4) cell formulas must be copied and pasted from a prescriptive measure that utilizes early retirement.
2. HVAC measures use early retirement: copy and paste the formulas from row 4792, columns K, L, AY, and AZ
3. The below tables shows the E3 reporting tool column headers that require inputs
4. The green cells are the summary values transferred from the project summary table
5. Below inputs are based the per measure average values.
Customer Sector | Measure | Climate Zone | Customer Rate Type | Category | Decision Type | Average Remaining Life of Equip. Replaced | Annual kWh Savings | Coincident Peak Savings (kW) | Measure Life | DEER Net to Gross Ratio Override | Measure Cost (per Cost Unit) | (Cost) Units Installed | Incentives Received by Customer ($/Unit) | Measure Type | Load Shape | Natural Replacement Costs | Early Retirement Cost | Natural Replacement Annual kWh Savings | Natural Replacement Coincident Peak Savings | Early Retirement Annual kWh Savings | Early Retirement Coincident Peak Savings | Annual kWh Savings | Coincident Peak Savings (kW)
Commercial | Lighting program | CZ04 | Commercial | Non-Res Lighting | Early Retirement | #DIV/0! | copy formula | copy formula | #DIV/0! | Optional | #DIV/0! | 0 | #DIV/0! | EE | Non-Res Lighting | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | copy formula | copy formula
Measure Calculations for Second Baseline
From Project Input Table | [7 empty] | Calculated values for second baseline
Existing Fixture Lamp Type | Quantity | New Fixture Lamp Type | Measure Lamp Description | Rebate | Energy Savings (KWh) | Peak DR (kW) | Enter EUL- default of 15 or measure-specific value | RUL | Energy Savings, second baseline | Peak DR, second baseline
| 0 | 0 | 0 | 0 | 0 | 0 | 15 | 5 | 0 | 0
| 0 | 0 | 0 | 0 | 0 | 0 | 15 | 5 | 0 | 0
| 0 | 0 | 0 | 0 | 0 | 0 | 15 | 5 | 0 | 0 |  | Participant Cost - Early Retirement
| 0 | 0 | 0 | 0 | 0 | 0 | 15 | 5 | 0 | 0 |  | Notes
| 0 | 0 | 0 | 0 | 0 | 0 | 15 | 5 | 0 | 0 |  | 1 | For ER, the participant cost = full measure cost - (full measure cost - incremental cost/(1+discount rate)^RUL, where the discount rate is: | [10 empty] | 5%
| 0 | 0 | 0 | 0 | 0 | 0 | 15 | 5 | 0 | 0 |  | 2 | Incremental cost can vary significantly depending on the type of retrofit. The initial estimate is 50% of full measure cost (see below calculation)
| 0 | 0 | 0 | 0 | 0 | 0 | 15 | 5 | 0 | 0 |  | 3 | Initial Estimate for incremental cost:
| 0 | 0 | 0 | 0 | 0 | 0 | 15 | 5 | 0 | 0 |  |  | Incremental cost is equal to the difference in costs between what was installed compared to what would have been installed. If what would have been installed was a replacement of the same preexisting lighting type, then the cost is equal to the difference between the installed equipment and the replacement option. The implicit assumption is the labor costs would be the same for both options. If a code-compliant lighting type would have been installed, then the cost is equal to the difference between the installed equipment and the code-compliant option. Incremental costs can vary, so the initial assumptions used to estimate the incremental cost as a percentage of the full measure cost is as follows:
| 0 | 0 | 0 | 0 | 0 | 0 | 15 | 5 | 0 | 0 | [13 empty] | Percent of Full Cost | Weighting
| 0 | 0 | 0 | 0 | 0 | 0 | 15 | 5 | 0 | 0
| 0 | 0 | 0 | 0 | 0 | 0 | 15 | 5 | 0 | 0 | [12 empty] | Installed equipment cost | 67%
| 0 | 0 | 0 | 0 | 0 | 0 | 15 | 5 | 0 | 0 | [12 empty] | a. Incremental cost is nearly equal to the cost of the installed equipment (baseline is simple lamp replacement) | 63.65% | 70% | 44.55%
| 0 | 0 | 0 | 0 | 0 | 0 | 15 | 5 | 0 | 0 | [12 empty] | b. Incremental cost is equal to cost of installed equipment compared to code-compliant equipment, and the difference is 30% | 20.1% | 30% | 6.03%
| 0 | 0 | 0 | 0 | 0 | 0 | 15 | 5 | 0 | 0 | [12 empty] | Incremental cost as a percent of full measure cost |  |  | 50.58%
| 0 | 0 | 0 | 0 | 0 | 0 | 15 | 5 | 0 | 0
| 0 | 0 | 0 | 0 | 0 | 0 | 15 | 5 | 0 | 0
| 0 | 0 | 0 | 0 | 0 | 0 | 15 | 5 | 0 | 0 |  | Second baseline savings reduction factor for different existing fixture types
| 0 | 0 | 0 | 0 | 0 | 0 | 15 | 5 | 0 | 0 |  | T8_HP_4ft | 10% | Assumes T24 control requirements apply and reduces savings potential for a majority of the rebated projects (above code measure)
| 0 | 0 | 0 | 0 | 0 | 0 | 15 | 5 | 0 | 0 |  | T8_4ft | 10% | Assumes T24 control requirements apply and reduces savings potential for a majority of the rebated projects (above code measure)
| 0 | 0 | 0 | 0 | 0 | 0 | 15 | 5 | 0 | 0 |  | T8_all_other_lengths | 10% | Assumes T24 control requirements apply and reduces savings potential for a majority of the rebated projects (above code measure)
| 0 | 0 | 0 | 0 | 0 | 0 | 15 | 5 | 0 | 0 |  | LED | 1e-08% | Assumes preexisting fixture meets/exceeds code requirements (above code measure)
| 0 | 0 | 0 | 0 | 0 | 0 | 15 | 5 | 0 | 0 |  | CFL | 1e-06% | Assumes preexisting fixture meets/exceeds code requirements (above code measure)
| 0 | 0 | 0 | 0 | 0 | 0 | 15 | 5 | 0 | 0 |  | T5_Lamp | 1e-06% | Assumes preexisting fixture meets/exceeds code requirements (above code measure)
| 0 | 0 | 0 | 0 | 0 | 0 | 15 | 5 | 0 | 0 |  | T12_Lamp | 100% | Assumes the measure installed marginally meets code requirements or is ISP (below code measure)
| 0 | 0 | 0 | 0 | 0 | 0 | 15 | 5 | 0 | 0 |  | Incandescent | 100% | Assumes measure installed is required by state (T20) and federal code (EISA) requirements, or is ISP (below code measure)
| 0 | 0 | 0 | 0 | 0 | 0 | 15 | 5 | 0 | 0 |  | HPS | 20% | Assumes older fixture is replaced and T24 control requirements apply (below and above code measure)
| 0 | 0 | 0 | 0 | 0 | 0 | 15 | 5 | 0 | 0 |  | MH | 20% | Assumes older metal halide fixture is replaced and T24 control requirements apply (below and above code measure)
| 0 | 0 | 0 | 0 | 0 | 0 | 15 | 5 | 0 | 0 |  | Fluorescent | 100% | Assumes measure installed is required by state (T20) and federal code (EISA) requirements, or is ISP (below code measure)
| 0 | 0 | 0 | 0 | 0 | 0 | 15 | 5 | 0 | 0 |  | Exit_Sign | 100% | Assumes measure installed is required by state (T20) and federal code (EISA) requirements, or is ISP (below code measure)
| 0 | 0 | 0 | 0 | 0 | 0 | 15 | 5 | 0 | 0 |  | Misc | 100% | Assumes measure installed is required by state (T20) and federal code (EISA) requirements, or is ISP (below code measure)
| 0 | 0 | 0 | 0 | 0 | 0 | 15 | 5 | 0 | 0 |  | User-defined | 100% | Assumes measure installed is required by state (T20) and federal code (EISA) requirements, or is ISP (below code measure)
| 0 | 0 | 0 | 0 | 0 | 0 | 15 | 5 | 0 | 0
| 0 | 0 | 0 | 0 | 0 | 0 | 15 | 5 | 0 | 0
| 0 | 0 | 0 | 0 | 0 | 0 | 15 | 5 | 0 | 0
| 0 | 0 | 0 | 0 | 0 | 0 | 15 | 5 | 0 | 0
| 0 | 0 | 0 | 0 | 0 | 0 | 15 | 5 | 0 | 0
| 0 | 0 | 0 | 0 | 0 | 0 | 15 | 5 | 0 | 0
| 0 | 0 | 0 | 0 | 0 | 0 | 15 | 5 | 0 | 0
Project Total | 0 | 0 |  | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0
Notes:
1. Existing lamp or fixture type - used to determine savings reduction factor. See the below table for the drop box options.
2. The second baseline savings is estimated by multipying the savings reduction factor by the first year savings.
1. EUL and RUL totals are weighted averages.
2. RUL = EUL/3
3. Energy savings, second baseline = energy savings (kWh) - (energy savings (kWh) * Savings reduction factor for existing lamp type)
4. Demand reduction, second baseline = Peak demand reduction (kW) - (Peak demand reduction (kW)* savings reduction factor for existing lamp type)
5. Participant cost test for accelerated replacement - see Participant Cost notes for formula and input assumptions
Determining EUL and RUL:
The default EUL for lighting measures is 15 years. A measure-specific EUL can be determined by dividing the lamp effective rated life by the lighting annual occupancy hours, limited to a maximum of 5 years.

## Lighting Database
CFL | Total | [5 empty] | SPC Reference Codes
Lamp Name | Watts | Lamp Number | Retrofit1 | Retrofit2 | Retrofit3 | Notes | LAMP CODE | BALLAST TYPE | NOM. W/LAMP | LAMP/ FIXT | DESCRIPTION | Lamp | Ballast Type2 | Output | Ballast Wiring | kW/ FIXT
CFL, 5W, screw base | 5
CFL, 7W, screw base | 7
CFL, 9W, screw base | 9
CFL, 11W, screw base | 11
CFL, 13W, screw base | 13
CFL, 15W, screw base | 15
CFL, 17W, screw base | 17
CFL, 18W, screw base | 18
CFL, 20W, screw base | 20
CFL, 23W, screw base | 23
CFL, 30W, screw base | 30
CFL 32W, screw base | 32
CFL, 42W, screw base | 42
CFL, 53W, screw base | 53
CFL, 10W, quad, mag ballast | 15 | [5 empty] | CFQ10/1 | Mag-STD | 10 | 1
CFL, 13W, mag ballast | 17 | [5 empty] | CFQ13/1 | Mag-STD | 13 | 1 |  | Compact Fluorescent, quad, (1) 13W lamp |  |  |  | 0.017
CFL, 13W, electronic ballast | 15 | [5 empty] | CFQ13/1-L | Electronic | 13 | 1
CFL, 13W, quad, 2-lamp, electronic ballast | 29 | [5 empty] | CFQ13/2-L | Electronic | 13 | 2
CFL, 13W, quad, 2-lamp, mag ballast | 31 | [5 empty] | CFQ13/2 | Mag-STD | 13 | 2
CFL, 13W, quad, 3-lamp mag ballast | 48 | [5 empty] | CFQ13/3 | Mag-STD | 13 | 3
CFL, 15W, quad, mag ballast | 20 | [5 empty] | CFQ15/1 | Mag-STD | 15 | 1
CFL, 16W, 2D lamp | 26 | [5 empty] | CF16/2D | Mag-STD |  | 1 |  | Compact Fluorescent, 2D, (1) 16W lamp |  |  |  | 0.026
CFL, 17W, quad, mag ballast | 24 | [5 empty] | CFQ17/1 | Mag-STD | 17 | 1
CFL, 17W, quad, 2-lamp, mag ballast | 48 | [5 empty] | CFQ17/2 | Mag-STD | 17 | 2
CFL, 18W, quad, mag ballast | 23 | [5 empty] | CFQ18/1 | Mag-STD | 18 | 1
CFL, 18W, pin base | 26 | [5 empty] | CFQ18/1 | Mag-STD |  | 1 |  | Compact Fluorescent, quad, (1) 18W lamp |  |  |  | 0.026
CFL, 18W, pin base, electronic ballast | 20 | [5 empty] | CFQ18/1-L | Electronic |  | 1 |  | Compact Fluorescent, quad, (1) 18W lamp, BF=1.0 |  |  |  | 0.02
CFL, 18W, quad, electronic ballast | 20 | [5 empty] | CFQ18/1-L | Electronic | 18 | 1
CFL, 18W, quad, 2-lamp, mag ballast | 44 | [5 empty] | CFQ18/2 | Mag-STD | 18 | 2
CFL, 18W, quad, 2-lamp, electronic ballast | 36 | [5 empty] | CFQ18/2-L | Electronic | 18 | 2
CFL, 20W, quad, mag ballast | 23 | [5 empty] | CFQ20/1 | Mag-STD | 20 | 1
CFL, 20W, quad, 2-lamp, mag ballast | 46 | [5 empty] | CFQ20/2 | Mag-STD | 20 | 2
CFL, 22W, quad, mag ballast | 24 | [5 empty] | CFQ22/1 | Mag-STD | 22 | 1
CFL, 22W, quad, 2-lamp, mag ballast | 48 | [5 empty] | CFQ22/2 | Mag-STD | 22 | 2
CFL, 22W, quad, 3-lamp, mag ballast | 72 | [5 empty] | CFQ22/3 | Mag-STD | 22 | 3
CFL, 26W, quad, mag ballast | 33 | [5 empty] | CFQ26/1 | Mag-STD | 26 | 1
CFL, 26W, quad, electronic ballast | 28 | [5 empty] | CFQ26/1-L | Electronic | 26 | 1
CFL, 26W, quad, 2-lamp, mag ballast | 66 | [5 empty] | CFQ26/2 | Mag-STD | 26 | 2
CFL, 26W, quad, 2-lamp, electronic ballast | 52 | [5 empty] | CFQ26/2-L | Electronic | 26 | 2
CFL, 26W, quad, 3-lamp, mag ballast | 99 | [5 empty] | CFQ26/3 | Mag-STD | 26 | 3
CFL, 26W, quad, 6-lamp, , electronic ballast | 150 | [5 empty] | CFQ26/6-L | Electronic | 26 | 6
CFL, 32W, quad, electronic ballast | 34 | [5 empty] | CFT32/1-L | Electronic | 32 | 1
CFL, 32W, quad, 2-lamp, electronic ballast | 62 | [5 empty] | CFT32/2-L | Electronic | 32 | 2
CFL, 40W, quad, electronic ballast | 43 | [5 empty] | CFT40/1-L | Electronic | 40 | 1
CFL, 40W, quad, 2-lamp, electronic ballast | 72 | [5 empty] | CFT40/2-L | Electronic | 40 | 2
CFL, 50W, twin, electronic ballast | 61 | [5 empty] | CFT50/1-L | Electronic | 50 | 1
CFL, 55W, twin, electronic ballast, BF<0.94 | 59 | [5 empty] | CFT55/1-L | Electronic | 55 | 1
CFL, 57W, triple, electronic ballast, BF=0.94 | 60 | [5 empty] | CFTR57/1-L | Electronic | 57 | 1
T12_Lamp | Total | [5 empty] | SPC Reference Codes
Lamp Name | Baseline Watts | Lamp Number | Retrofit1 | Retrofit2 | Retrofit3 | ACTUAL WATTAGE | LAMP CODE | BALLAST TYPE | NOM. W/LAMP | Lamp/Fixt | Description | Lamp | Ballast Type2 | Output | Ballast Wiring | kW/ FIXT
Fluorescent, 18" T12 lamp | 19 |  |  |  |  | 19
Fluorescent, 18" (2) T12 lamps | 38 |  |  |  |  | 38
Fluorescent, 24" T12 lamp | 29 |  |  |  |  | 28
Fluorescent, 24" (2) T12 lamps | 56 |  |  |  |  | 56
Fluorescent, 24" (3) T12 lamps | 68 |  |  |  |  | 68
Fluorescent, 24" (4) T12 lamps | 100 |  |  |  |  | 100
Fluorescent, 36" (2) T12 lamps | 50 |  |  |  |  | 64
Fluorescent, 48" T12 lamp | 44 |  | Occupancy sensor, T12 lamp |  |  | 50
Fluorescent, 48" (2) T12 lamps | 74 |  |  |  |  | 96
Fluorescent, 48" (3) T12 lamps | 114 |  | (3) T12 lamps to (3) T8 lamps - 4' fluorescent | (3) T12 lamps to (2) T8 lamps - 4' fluorescent | Occupancy sensor, T12 lamp | 135
Fluorescent, 48" (4) T12 lamps | 148 |  | (4) T12 lamps to (4) T8 lamps - 4' fluorescent | (4) T12 lamps to (3) T8 lamps - 4' fluorescent | Occupancy sensor, T12 lamp | 180
Fluorescent, 48" (6) T12 lamps | 216 |  | New High Bay fixture, (6) lamp T8 - 4' lamps |  | Occupancy sensor, T12 lamp | 260
Fluorescent, 60" T12 lamp | 63 |  |  |  |  | 63
Fluorescent, 60" T12 HO lamp | 92 |  | 5' T12 HO to 25w refrigerated case LED with OS |  |  | 92
Fluorescent, 60" (2) T12 lamps | 126 |  |  |  |  | 126
Fluorescent, 60" (2) T12 HO lamps | 184 |  |  |  |  | 184
Fluorescent, 60" (4) T12 lamps | 226
Fluorescent, 96" T12 lamp | 90 |  |  |  |  | 90
Fluorescent, 96" T12 lamp, HO | 110 |  |  |  |  | 110
Fluorescent, 96" (2) T12 lamps | 165 |  | (2) T12 lamps to (4) 4' T8 lamps |  |  | 165
Fluorescent, 96" (2) T12 lamp, HO | 205 |  | (2) T12 lamps to (4) 4' T8 lamps |  |  | 205
Fluorescent, 96" (4) T12 lamps | 330 |  | (4) T12 lamps to (2) T8 lamps - 8' fluorescent |  |  | 330
T8_4ft | Total | [5 empty] | SPC Reference Codes
Lamp Name | Watts | Lamp Number | Retrofit1 | Retrofit2 | Retrofit3 | Notes | FIXT CODE | LAMP CODE | NOM. W/LAMP | LAMP/ FIXT | DESCRIPTION | Lamp | Ballast Type2 | Output | Sort Order | kW/ FIXT
Bi-level stairwell, hallway, and garage fixture w/ oc, 2-lamp T8 | 48.4 | [5 empty] | Average hourly wattage - 69% of time at 62 W and 31% of time at 18 W, based on 2 lamp, 4ft T8 fixture with integrated occupancy sensor with fail safe mode | [7 empty] | 1
Fluorescent 48", (1) T8 lamp, BF normal | 29 | [5 empty] | F41ILL | F32T8-STD | 32 | 1 | 78 CRI, 24,000 Hr., ISR, Fluorescent, (1) 48", T-8 lamp,IS Ballast, NLO |  | Electronic
Fluorescent 48", (1) T8 lamp, BF <85 | 25 | [5 empty] | F41ILL/T2-R | F32T8-STD | 32 | 1 | 78 CRI, 24,000 Hr., ISR, Fluorescent, (1) 48", T-8 lamp,IS Ballast, RLO, Tandem 2 Lamp Ballast |  | Electronic
Fluorescent 48", (1) T8 lamps, BF 0.96-1.1 | 33 | [5 empty] | F41ILL/T2-H | F32T8-STD | 32 | 1 | 78 CRI, 24,000 Hr., ISR, Fluorescent, (1) 48", T-8 lamp,IS Ballast, HLO, Tandem 2 Lamp Ballast |  | Electronic
Fluorescent 48", (2) T8 lamps, BF normal | 56 | [5 empty] | F42ILL/T4 | F32T8-STD | 32 | 2 | 78 CRI, 24,000 Hr., ISR, Fluorescent, (2) 48", T-8 lamp,IS Ballast, NLO, Tandem 4 Lamp Ballast |  | Electronic
Fluorescent 48", (2) T8 lamps, BF <0.85 | 49 | [5 empty] | F42ILL/T4-R | F32T8-STD | 32 | 2 | 78 CRI, 24,000 Hr., ISR, Fluorescent, (2) 48", T-8 lamp,IS Ballast, RLO, Tandem 4 Lamp Ballast |  | Electronic
Fluorescent 48", (2) T8 lamps, BF >1.0 | 65 | [5 empty] | F42ILL-H | F32T8-STD | 32 | 2 | 78 CRI, 24,000 Hr., ISR, Fluorescent, (2) 48", T-8 lamp,IS Ballast, HLO |  | Electronic
Fluorescent 48", (3) T8 lamps, BF normal | 84 | [5 empty] | F43ILL | F32T8-PREM | 32 | 3 | 85 CRI, 30,000 Hr., ISR, Fluorescent, (3) 48", T-8 lamp,IS Ballast, NLO |  | Electronic
Fluorescent 48", (3) T8 lamps, BF <0.85 | 74 | [5 empty] | F43ILL-R | F32T8-PREM | 32 | 3 | 85 CRI, 30,000 Hr., ISR, Fluorescent, (3) 48", T-8 lamp,IS Ballast, RLO |  | Electronic
Fluorescent 48", (3) T8 lamps, BF >1.0 | 93 | [5 empty] | F43ILL-H | F32T8-PREM | 32 | 3 | 85 CRI, 30,000 Hr., ISR, Fluorescent, (3) 48", T-8 lamp,IS Ballast, HLO |  | Electronic
Fluorescent, 48" (4) T8 lamps, BF normal | 112 | [5 empty] | F44ILL | F32T8-STD | 32 | 4 | 78 CRI, 24,000 Hr., ISR, Fluorescent, (4) 48", T-8 lamp,IS Ballast, NLO |  | Electronic
Fluorescent, 48" (4) T8 lamps, BF<0.85 | 98 | [5 empty] | F44ILL-R | F32T8-STD | 32 | 4 | 78 CRI, 24,000 Hr., ISR, Fluorescent, (4) 48", T-8 lamp,IS Ballast, RLO |  | Electronic
Fluorescent, 48" (4) T8 lamps, BF >1.1 | 155 | [5 empty] | F44ILL/2-V | F32T8-STD | 32 | 4 | 78 CRI, 24,000 Hr., ISR, Fluorescent, (4) 48", T-8 lamp, (2) IS Ballast, VHLO |  | Electronic
Fluorescent, 48" (6) T8 lamps, BF normal | 168 | [5 empty] | F46ILL/2 | F32T8-STD | 32 | 6 | 78 CRI, 24,000 Hr., ISR, Fluorescent, (6) 48", T-8 lamp, (2) IS Ballast, NLO |  | Electronic
Fluorescent, 48" (6) T8 lamps, BF <0.85 | 146 | [5 empty] | F46ILLE/2-R | F32T8-PREM | 32 | 6 | 85 CRI, 30,000 Hr., ISR, Fluorescent, (6) 48", T-8 lamp, (2) Premium IS Ballast, RLO |  | Elec-Prem
Fluorescent, 48" (6) T8 lamps, BF >1.0 | 227 | [5 empty] | F46ILL/2-V | F32T8-STD | 32 | 6 | 78 CRI, 24,000 Hr., ISR, Fluorescent, (6) 48", T-8 lamp, (2) IS Ballast, VHLO |  | Electronic
T8_HP_4ft | Total | [5 empty] | SPC Reference Codes
Lamp Name | Watts | Lamp Number | Retrofit1 | Retrofit2 | Retrofit3 | Notes | FIXT CODE | LAMP CODE | NOM. W/LAMP | LAMP/ FIXT | Fixture Code | Lamp | Ballast Type2 | Output | Ballast Wiring | kW/ FIXT
Fluorescent, 48" (1) 32W HPT8 lamp, BF normal | 28 |  |  |  |  | 1 | F41WLLE | F32T8-PREM | 32 | 1 | 85 CRI, 30,000 Hr., ISR, Fluorescent, (1) 48", T-8 lamp,Premium IS Ballast, NLO |  | Elec-Prem
Fluorescent, 48" (1) 32W HPT8 lamp, BF<0.85 | 25 |  |  |  |  | 2 | F41WLLE-R | F32T8-PREM | 32 | 1 | 85 CRI, 30,000 Hr., ISR, Fluorescent, (1) 48", T-8 lamp,Premium IS Ballast, RLO |  | Elec-Prem
Fluorescent, 48" (2) 32W HPT8 lamps, BF normal | 55 |  |  |  |  | 4 | F42ILLE | F32T8-PREM | 32 | 2 | 85 CRI, 30,000 Hr., ISR, Fluorescent, (2) 48", T-8 lamp,Premium IS Ballast, NLO |  | Elec-Prem
Fluorescent, 48" (2) 32W HPT8 lamps, BF <0.85 | 48 |  |  |  |  | 5 | F42WLLE-R | F32T8-PREM | 32 | 2 | 85 CRI, 30,000 Hr., ISR, Fluorescent, (2) 48", T-8 lamp,Premium IS Ballast, RLO |  | Elec-Prem
Fluorescent, 48" (2) 32W HPT8 lamp, BF 0.96-1.1 | 63 |  |  |  |  | 6 | F42WLLE-H | F32T8-PREM | 32 | 2 | 85 CRI, 30,000 Hr., ISR, Fluorescent, (2) 48", T-8 lamp,Premium IS Ballast, HLO |  | Elec-Prem
Fluorescent, 48" (2) 32W HPT8 lamp, BF >1.1 | 74 |  |  |  |  | 7 | F42WLLE-V | F32T8-PREM | 32 | 2 | 85 CRI, 30,000 Hr., ISR, Fluorescent, (2) 48", T-8 lamp,Premium IS Ballast, VHLO |  | Elec-Prem
Fluorescent, 48" (3) 32W HPT8 lamps, BF normal | 82 |  |  |  |  | 8 | F43WLLE | F32T8-PREM | 32 | 3 | 85 CRI, 30,000 Hr., ISR, Fluorescent, (3) 48", T-8 lamp,Premium IS Ballast, NLO |  | Elec-Prem
Fluorescent, 48" (3) 32W HPT8 lamps, BF <0.85 | 73 |  |  |  |  | 9 | F43WLLE-R | F32T8-PREM | 32 | 3 | 85 CRI, 30,000 Hr., ISR, Fluorescent, (3) 48", T-8 lamp,Premium IS Ballast, RLO |  | Elec-Prem
Fluorescent, 48" (3) 32W HPT8 lamp, BF 0.96-1.1 | 90 |  |  |  |  | 10 | F43WLLE-H | F32T8-PREM | 32 | 3 | 85 CRI, 30,000 Hr., ISR, Fluorescent, (3) 48", T-8 lamp,Premium IS Ballast, HLO |  | Elec-Prem
Fluorescent, 48" (3) 32W HPT8 lamp, BF >1.1 | 111 |  |  |  |  | 11 | F43WLLE-V | F32T8-PREM | 32 | 3 | 85 CRI, 30,000 Hr., ISR, Fluorescent, (3) 48", T-8 lamp,Premium IS Ballast, VHLO |  | Elec-Prem
Fluorescent, 48" (4) 32W HPT8 lamps, BF normal | 109 |  |  |  |  | 12 | F44WLLE | F32T8-PREM | 32 | 4 | 85 CRI, 30,000 Hr., ISR, Fluorescent, (4) 48", T-8 lamp,Premium IS Ballast, NLO |  | Elec-Prem
Fluorescent, 48" (4) 32W HPT8 lamps, BF <0.85 | 96 |  |  |  |  | 13 | F44WLLE-R | F32T8-PREM | 32 | 4 | 85 CRI, 30,000 Hr., ISR, Fluorescent, (4) 48", T-8 lamp,Premium IS Ballast, RLO |  | Elec-Prem
Fluorescent, 48" (4) 32W HPT8 lamp, BF 0.96-1.1 | 114 |  |  |  |  | 14 | F44WLLE-H | F32T8-PREM | 32 | 4 | 85 CRI, 30,000 Hr., ISR, Fluorescent, (4) 48", T-8 lamp,Premium IS Ballast, HLO |  | Elec-Prem
Fluorescent, 48" (4) 32W HPT8 lamp, BF >1.1 | 146 |  |  |  |  | 15 | F44WLLE-V | F32T8-PREM | 32 | 4 | 85 CRI, 30,000 Hr., ISR, Fluorescent, (4) 48", T-8 lamp,Premium IS Ballast, VHLO |  | Elec-Prem
Fluorescent, 48" (6) 32W HPT8 lamps, BF normal | 164 |  |  |  |  | 16 | F46WLLE/2 | F32T8-PREM | 32 | 6 | 85 CRI, 30,000 Hr., ISR, Fluorescent, (6) 48", T-8 lamp, (2) Premium IS Ballast, NLO |  | Elec-Prem
Fluorescent, 48" (6) 32W HPT8 lamps, BF <0.85 | 146 |  |  |  |  | 17 | F46WLLE/2-R | F32T8-PREM | 32 | 6 | 85 CRI, 30,000 Hr., ISR, Fluorescent, (6) 48", T-8 lamp, (2) Premium IS Ballast, RLO |  | Elec-Prem
Fluorescent, 48" (6) 32W HPT8 lamps, BF >1.1 | 227 |  |  |  |  | 17 | F46WLLE/2-V | F32T8-PREM | 32 | 6 | 85 CRI, 30,000 Hr., ISR, Fluorescent, (6) 48", T-8 lamp, (2) Premium IS Ballast, VHLO |  | Elec-Prem
Fluorescent, 48" (2) 28W HPT8 lamps, BF normal | 48 |  |  |  |  | 31 | F42WLLE | F28T8-PREM | 28 | 2 | 85 CRI, 30,000 Hr., ISR, Fluorescent, (2) 48", T-8 lamp,Premium IS Ballast, NLO |  | Elec-Prem
Fluorescent, 48" (2) 28W HPT8 lamps, BF <0.85 | 42 |  |  |  |  | 32 | F42WLLE-R | F28T8-PREM | 28 | 2 | 85 CRI, 30,000 Hr., ISR, Fluorescent, (2) 48", T-8 lamp,Premium IS Ballast, RLO |  | Elec-Prem
Fluorescent, 48" (2) 28W HPT8 lamp, BF 0.96-1.1 | 53 |  |  |  |  | 33 | F42WLLE-H | F28T8-PREM | 28 | 2 | 85 CRI, 30,000 Hr., ISR, Fluorescent, (2) 48", T-8 lamp,Premium IS Ballast, HLO |  | Elec-Prem
Fluorescent, 48" (2) 28W HPT8 lamp, BF >1.1 | 65 |  |  |  |  | 34 | F42WLLE-V | F28T8-PREM | 28 | 2 | 85 CRI, 30,000 Hr., ISR, Fluorescent, (2) 48", T-8 lamp,Premium IS Ballast, VHLO |  | Elec-Prem
Fluorescent, 48" (3) 28W HPT8 lamps, BF normal | 71 |  |  |  |  | 35 | F43WLLE | F28T8-PREM | 28 | 3 | 85 CRI, 30,000 Hr., ISR, Fluorescent, (3) 48", T-8 lamp,Premium IS Ballast, NLO |  | Elec-Prem
Fluorescent, 48" (3) 28W HPT8 lamps, BF <0.85 | 64 |  |  |  |  | 36 | F43WLLE-R | F28T8-PREM | 28 | 3 | 85 CRI, 30,000 Hr., ISR, Fluorescent, (3) 48", T-8 lamp,Premium IS Ballast, RLO |  | Elec-Prem
Fluorescent, 48" (3) 28W HPT8 lamp, BF 0.96-1.1 | 76 |  |  |  |  | 37 | F43WLLE-H | F28T8-PREM | 28 | 3 | 85 CRI, 30,000 Hr., ISR, Fluorescent, (3) 48", T-8 lamp,Premium IS Ballast, HLO |  | Elec-Prem
Fluorescent, 48" (3) 28W HPT8 lamp, BF >1.1 | 97 |  |  |  |  | 38 | F43WLLE-V | F28T8-PREM | 28 | 3 | 85 CRI, 30,000 Hr., ISR, Fluorescent, (3) 48", T-8 lamp,Premium IS Ballast, VHLO |  | Elec-Prem
Fluorescent, 48" (4) 28W HPT8 lamps, BF normal | 95 |  |  |  |  | 39 | F44WLLE | F28T8-PREM | 28 | 4 | 85 CRI, 30,000 Hr., ISR, Fluorescent, (4) 48", T-8 lamp,Premium IS Ballast, NLO |  | Elec-Prem
Fluorescent, 48" (4) 28W HPT8 lamps, BF <0.85 | 85 |  |  |  |  | 40 | F44WLLE-R | F28T8-PREM | 28 | 4 | 85 CRI, 30,000 Hr., ISR, Fluorescent, (4) 48", T-8 lamp,Premium IS Ballast, RLO |  | Elec-Prem
Fluorescent, 48" (4) 28W HPT8 lamp, BF 0.96-1.1 | 107 |  |  |  |  | 41 | F44WLLE-H | F28T8-PREM | 28 | 4 | 85 CRI, 30,000 Hr., ISR, Fluorescent, (4) 48", T-8 lamp,Premium IS Ballast, HLO |  | Elec-Prem
Fluorescent, 48" (4) 28W HPT8 lamp, BF >1.1 | 128 |  |  |  |  | 42 | F44WLLE-V | F28T8-PREM | 28 | 4 | 85 CRI, 30,000 Hr., ISR, Fluorescent, (4) 48", T-8 lamp,Premium IS Ballast, VHLO |  | Elec-Prem
Fluorescent, 48" (1) 25W HPT8 lamp, BF normal | 24 |  |  |  |  | 43 | F41WLL | F28T8-PREM-ES | 25 | 1 | 85 CRI, 30,000 Hr., ISR, Fluorescent, (1) 48", T-8 lamp,IS Ballast, NLO |  | Electronic
Fluorescent, 48" (2) 25W HPT8 lamps, BF normal | 44 |  |  |  |  | 44 | F42WLLE | F28T8-PREM-ES | 25 | 2 | 85 CRI, 30,000 Hr., ISR, Fluorescent, (2) 48", T-8 lamp,Premium IS Ballast, NLO |  | Elec-Prem
Fluorescent, 48" (2) 25W HPT8 lamps, BF <0.85 | 38 |  |  |  |  | 45 | F42WLLE-R | F28T8-PREM-ES | 25 | 2 | 85 CRI, 30,000 Hr., ISR, Fluorescent, (2) 48", T-8 lamp,Premium IS Ballast, RLO |  | Elec-Prem
Fluorescent, 48" (2) 25W HPT8 lamp, BF 0.96-1.1 | 50 |  |  |  |  | 46 | F42WLLE-H | F28T8-PREM-ES | 25 | 2 | 85 CRI, 30,000 Hr., ISR, Fluorescent, (2) 48", T-8 lamp,Premium IS Ballast, HLO |  | Elec-Prem
Fluorescent, 48" (3) 25W HPT8 lamps, BF normal | 65 |  |  |  |  | 47 | F43WLLE | F28T8-PREM-ES | 25 | 3 | 85 CRI, 30,000 Hr., ISR, Fluorescent, (3) 48", T-8 lamp,Premium IS Ballast, NLO |  | Elec-Prem
Fluorescent, 48" (3) 25W HPT8 lamps, BF <0.85 | 58 |  |  |  |  | 48 | F43WLLE-R | F28T8-PREM-ES | 25 | 3 | 85 CRI, 30,000 Hr., ISR, Fluorescent, (3) 48", T-8 lamp,Premium IS Ballast, RLO |  | Elec-Prem
Fluorescent, 48" (3) 25W HPT8 lamp, BF 0.96-1.1 | 70 |  |  |  |  | 49 | F43WLLE-H | F28T8-PREM-ES | 25 | 3 | 85 CRI, 30,000 Hr., ISR, Fluorescent, (3) 48", T-8 lamp,Premium IS Ballast, HLO |  | Elec-Prem
Fluorescent, 48" (3) 25W HPT8 lamp, BF >1.1 | 91 |  |  |  |  | 50 | F43WLLE-V | F28T8-PREM-ES | 25 | 3 | 85 CRI, 30,000 Hr., ISR, Fluorescent, (3) 48", T-8 lamp,Premium IS Ballast, VHLO |  | Elec-Prem
Fluorescent, 48" (4) 25W HPT8 lamps, BF normal | 86 |  |  |  |  | 51 | F44WLLE | F28T8-PREM-ES | 25 | 4 | 85 CRI, 30,000 Hr., ISR, Fluorescent, (4) 48", T-8 lamp,Premium IS Ballast, NLO |  | Elec-Prem
Fluorescent, 48" (4) 25W HPT8 lamps, BF <0.85 | 77 |  |  |  |  | 52 | F44WLLE-R | F28T8-PREM-ES | 25 | 4 | 85 CRI, 30,000 Hr., ISR, Fluorescent, (4) 48", T-8 lamp,Premium IS Ballast, RLO |  | Elec-Prem
Fluorescent, 48" (4) 25W HPT8 lamp, BF 0.96-1.1 | 99 |  |  |  |  | 53 | F44WLLE-H | F28T8-PREM-ES | 25 | 4 | 85 CRI, 30,000 Hr., ISR, Fluorescent, (4) 48", T-8 lamp,Premium IS Ballast, HLO |  | Elec-Prem
Fluorescent, 48" (4) 25W HPT8 lamp, BF >1.1 | 119 |  |  |  |  | 54 | F44WLLE-V | F28T8-PREM-ES | 25 | 4 | 85 CRI, 30,000 Hr., ISR, Fluorescent, (4) 48", T-8 lamp,Premium IS Ballast, VHLO |  | Elec-Prem
Fluorescent, 48" (1) 25W HPT8 lamp, BF normal | 25 |  |  |  |  | 55 | F41WLLE | F28T8-PREM | 28 | 1 | 85 CRI, 30,000 Hr., ISR, Fluorescent, (1) 48", T-8 lamp,Premium IS Ballast, NLO |  | Elec-Prem
T8_all other lengths | Total | [5 empty] | SPC Reference Codes
Lamp Name | Watts | Lamp Number | Retrofit1 | Retrofit2 | Retrofit3 | Notes | LAMP CODE | BALLAST TYPE | NOM. W/LAMP | LAMP/ FIXT | DESCRIPTION | Lamp | Ballast Type2 | Output | Ballast Wiring | kW/ FIXT
Fluorescent, 18" T8 lamp | 19 | 700 |  |  |  | Updated 3/24/2010 | F15T8 | Mag-STD | 15 | 1 | Fluorescent, (1) 18" | T-8 lamp |  |  |  | 0.019
Fluorescent, 24" T8 lamp | 20 | 705 |  |  |  | Updated 3/24/2010 | F17T8 | Electronic | 17 | 1 | Fluorescent, (1) 24" | T-8 lamp | Instant Start Ballast | NLO " |  | 0.02
Fluorescent, 24" (2) T8 lamps | 31 | 715 |  |  |  | Updated 3/24/2010 | F17T8 | Electronic | 17 | 2 | Fluorescent, (2) 24" | T-8 lamp | Rapid Start Ballast | NLO " |  | 0.031
Fluorescent, 24" (3) T8 lamps, BF 0.96-1.1 | 48 | 725 |  |  |  | Updated 3/24/2010 | F17T8 | Electronic | 17 | 3 | Fluorescent, (3) 24" | T-8 lamp | Instant Start Ballast | HLO " |  | 0.049
Fluorescent, 24" (4) T8 lamps | 66 | 735 |  |  |  | Updated 3/24/2010 | F17T8 | Electronic | 17 | 4 | Fluorescent, (4) 24" | T-8 lamp | Rapid Start Ballast | NLO " |  | 0.068
Fluorescent, 36" (2) T8 lamps | 46 | 745 |  |  |  | Updated 3/24/2010 | F25T8 | Electronic | 25 | 2 | Fluorescent, (2) 36" | T-8 lamp | Instant Start Ballast | NLO " |  | 0.046
Fluorescent, 60" T8 lamp, BF-normal | 36 | 875 |  |  |  | Updated 3/24/2010 | F40T8 | Electronic | 40 | 1 | Fluorescent, (1) 60" |  | Instant Start Ballast | NLO |  | 0.036
Fluorescent, 60", T8 lamp, BF-HO | 57 | 877 |  |  |  |  | F51ILL-V | Electronic | 40 | 1 | Fluorescent, (1) 60" | T-8 lamp
Fluorescent, 60", (2) T8 lamps, BF-VHLO | 102 | 877.5 |  |  |  |  | F52ILL-V | F40T8 | 40 | 2 | Fluorescent, (2) 60",T8 lamp, IS Ballast, VHLO |  | Electronic
Fluorescent, 60", T12 HO (refrig. display case) | 69 | 878 |  |  |  |  | F51SHL | F60T12/HO | 75 | 1 | Fluorescent, (1) 60", STD HO lamp |  | Electronic
Fluorescent, 60" (2) T12 HO (refrig. display case) | 132 | 879 |  |  |  |  | F52SHL | F60T12/HO | 75 | 2 | Fluorescent, (2) 60", STD HO lamp |  | Electronic
Fluorescent, 60" (2) T8 lamps | 72 | 880 |  |  |  | Updated 3/24/2010 | F40T8 | Electronic | 40 | 2 | Fluorescent, (2) 60" |  | Instant Start Ballast | NLO |  | 0.072
Fluorescent, 60" (4) T8 lamps | 134 | 885 |  |  |  | Updated 3/24/2010 | F40T8 | Electronic | 40 | 4 | Fluorescent, (3) 60" |  | Instant Start Ballast | NLO |  | 0.134
Fluorescent, 72", T12 HO (refrig. display case) | 120 | 888 |  |  |  |  | F61SHS | F72T12/HO | 85 | 1 | Fluorescent, (1) 72", STD HO lamp |  | Mag-STD
Fluorescent, 72" (2) T12 HO (refrig. display case) | 194 | 889 |  |  |  |  | F62SHE | F72T12/HO | 85 | 2 | Fluorescent, (2) 72", STD HO lamp |  | Mag-ES
Fluorescent, 96" (2) T8 lamps, BF<0.85 | 98 | 890 |  |  |  | BF < 0.85 Updated 3/24/2010 | F96T8 | Electronic | 59 | 1 | Fluorescent, (2) 96" | T-8 lamp | Instant Start Ballast | RLO |  | 0.098
Fluorescent, 96" (1) T8 lamp | 57 | 895 |  |  |  | Updated 3/24/2010 | F96T8 | Electronic | 59 | 1 | Fluorescent, (1) 96" | T-8 lamp | Instant Start Ballast | NLO " |  | 0.058
Fluorescent, 96" (4) T8 lamps | 220 | 900 |  |  |  | Updated 3/24/2010 | F96T8 | Electronic | 59 | 4 | Fluorescent, (4) 96" | T-8 lamp | Instant Start Ballast | NLO " |  | 0.219
T5_Lamp | Total | [5 empty] | SPC Reference Codes
Lamp Name | Watts | Lamp Number | Retrofit1 | Retrofit2 | Retrofit3 | Notes | FIXT CODE | LAMP CODE | NOM. W/LAMP | LAMP/ FIXT | DESCRIPTION | Lamp | Ballast Type2 | Output | Ballast Wiring | kW/ FIXT
Fluorescent, (1) 46", T5 lamp, BF normal | 32 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | F41PLE | F28T5 | 28 | Fluorescent, (1) 46", T5 lamp, Premium PRS Ballast, NLO |  |  | Elec-Prem
Fluorescent, (1) 46", T5 lamp, BF 0.96-1.1 | 45 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | F41PLE-H | F28T5 | 28 | Fluorescent, (1) 46", T5 lamp, Premium PRS Ballast, HLO |  |  | Elec-Prem
Fluorescent, (1) 46", T5 lamp, BF normal | 37 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | F41PLE | F28T5/ES | 26 | Fluorescent, (1) 46", T5 lamp, Premium PRS Ballast, NLO |  |  | Elec-Prem
Fluorescent, (1) 46", T5 lamp, BF 0.96-1.1 | 43 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | F41PLE-H | F28T5/ES | 26 | Fluorescent, (1) 46", T5 lamp, Premium PRS Ballast, HLO |  |  | Elec-Prem
Fluorescent, (2) 46", T5 lamp, BF normal | 62 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | F42PLE | F28T5 | 28 | Fluorescent, (2) 46", T5 lamp, Premium PRS Ballast, NLO |  |  | Elec-Prem
Fluorescent, (2) 46", T5 lamp, BF 0.96-1.1 | 72 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | F42PLE-H | F28T5 | 28 | Fluorescent, (2) 46", T5 lamp, Premium PRS Ballast, HLO |  |  | Elec-Prem
Fluorescent, (2) 46", T5 lamp, BF normal | 58 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | F42PLE | F28T5/ES | 26 | Fluorescent, (2) 46", T5 lamp, Premium PRS Ballast, NLO |  |  | Elec-Prem
Fluorescent, (2) 46", T5 lamp, BF >1.1 | 68 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | F42PLE-V | F28T5/ES | 26 | Fluorescent, (2) 46", T5 lamp, Premium PRS Ballast, VHLO |  |  | Elec-Prem
Fluorescent, (3) 46", T5 lamp, BF normal | 95 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | F43PLE/2 | F28T5 | 28 | Fluorescent, (3) 46", T5 lamp, (2) Premium PRS Ballast, NLO |  |  | Elec-Prem
Fluorescent, (4) 46", T5 lamp, BF normal | 123 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | F44PLE/2 | F28T5 | 28 | Fluorescent, (4) 46", T5 lamp, (2) Premium PRS Ballast, NLO |  |  | Elec-Prem
Fluorescent, (6) 46", T5 lamp, BF normal | 185 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | F46PLE/3 | F28T5 | 28 | Fluorescent, (6) 46", T5 lamp, (3) Premium PRS Ballast, NLO |  |  | Elec-Prem
Fluorescent, (8) 46", T5 lamp, BF normal | 247 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | F48PLE/4 | F28T5 | 28 | Fluorescent, (8) 46", T5 lamp, (4) Premium PRS Ballast, NLO |  |  | Elec-Prem
Fluorescent, (1) 46", T5/HO lamp, BF normal | 62 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | F41PHLE | F54T5/HO | 54 | Fluorescent, (1) 46", T5/HO lamp, Premium PRS Ballast, NLO |  |  | Elec-Prem
Fluorescent, (2) 46", T5/HO lamp, BF normal | 118 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | F42PHLE | F54T5/HO | 54 | Fluorescent, (2) 46", T5/HO lamp, Premium PRS Ballast, NLO |  |  | Elec-Prem
Fluorescent, (2) 46", 54W T5 lamp, BF | 107 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | F42PLE | F54T5/ES | 47 | Fluorescent, (2) 46", T5 lamp, Premium PRS Ballast, NLO |  |  | Elec-Prem
Fluorescent (3) 46" 54W T5/HO lamp | 182 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | F43PHLE/2 | F54T5/HO | 54 | Fluorescent, (3) 46", T5/HO lamp, (2) Premium PRS Ballast, NLO |  |  | Elec-Prem
Fluorescent (4) 46" 54W T5/HO lamp | 237 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | F44PHLE/2 | F54T5/HO | 54 | Fluorescent, (4) 46", T5/HO lamp, (2) Premium PRS Ballast, NLO |  |  | Elec-Prem
Fluorescent (6) 46" 54W T5/HO lamp | 355 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | F46PHLE/3 | F54T5/HO | 54 | Fluorescent, (6) 46", T5/HO lamp, (3) Premium PRS Ballast, NLO |  |  | Elec-Prem
Fluorescent (8) 46" 54W T5 /HO lamp | 473 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | F48PHLE/4 | F54T5/HO | 54 | Fluorescent, (8) 46", T5/HO lamp, (4) Premium PRS Ballast, NLO |  |  | Elec-Prem
Fluorescent, (1) 58", 80W T5/HO lamp | 91 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | F51PHLE | F80T5/HO | 80 | Fluorescent, (1) 58", T5/HO lamp, Premium PRS Ballast, NLO |  |  | Elec-Prem
Fluorescent, (1) 58", 35W T5 lamp | 41 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | F51PLE | F35T5 | 35 | Fluorescent, (1) 58", T5 lamp, Premium PRS Ballast, NLO |  |  | Elec-Prem
Fluorescent, (2) 58", 35W T5 lamp | 77 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | F52PLE | F35T5 | 35 | Fluorescent, (2) 58", T5 lamp, Premium PRS Ballast, NLO |  |  | Elec-Prem
Fluorescent, (3) 58", 35W T5 lamp | 121 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | F53PLE/2 | F35T5 | 35 | Fluorescent, (3) 58", T5 lamp, (2) Premium PRS Ballast, NLO |  |  | Elec-Prem
Fluorescent, (4) 58", 35W T5 lamp | 154 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | F54PLE/2 | F35T5 | 35 | Fluorescent, (4) 58", T5 lamp, (2) Premium PRS Ballast, NLO |  |  | Elec-Prem
Fluorescent, (6) 58", 35W T5 lamp | 231 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | F56PLE/3 | F35T5 | 35 | Fluorescent, (6) 58", T5 lamp, (3) Premium PRS Ballast, NLO |  |  | Elec-Prem
Fluorescent, (8) 58", 35W T5 lamp | 308 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | F58PLE/4 | F35T5 | 35 | Fluorescent, (8) 58", T5 lamp, (4) Premium PRS Ballast, NLO |  |  | Elec-Prem
Incandescent | Per Lamp | [5 empty] | SPC Reference Codes
Lamp Name | Watts | Lamp Number | Retrofit1 | Retrofit2 | Retrofit3 | Notes | FIXT CODE | LAMP CODE | NOM. W/LAMP | LAMP/ FIXT | DESCRIPTION | Lamp | Ballast Type2 | Output | Ballast Wiring | kW/ FIXT
Incandescent 40W equivalent (29W halogen) | 29
Incandescent 60W equivalent (43W halogen) | 43
Incandescent 75W equivalent (53W halogen) | 53
Incandescent 100W equivalent (72W halogen) | 72
Incandescent 15W | 15 | 1100 | [5 empty] | I15 | 15 | 1 | [5 empty] | 0.015
Incandescent 25W | 25 | 1110 | [5 empty] | I25 | 25 | 1 | [5 empty] | 0.025 | Traditional Wattage | New Maximum Wattage | Lumens | Implementation Date
Incandescent 45W | 45 | 1120 | [5 empty] | I45 | 45 | 1 | [5 empty] | 0.045 | 100 | 72 | 1490-2600 | 40544
Incandescent 50W | 50 | 1170 | 50w incandescent to 7w LED downlight screw base lamp |  |  |  |  | I50 | 50 | 1 | [5 empty] | 0.05 | 75 | 53 | 1050-1489 | 40909
Incandescent 60W | 60 | 1180 | 60w incandescent to 18w CFL | 60w incandescent to 10w LED downlight screw base lamp |  |  |  | I60 | 60 | 1 | [5 empty] | 0.06 | 60 | 43 | 750-1049 | 41275
Incandescent 65W | 65 | 1190 | [5 empty] | I65 | 65 | 1 | [5 empty] | 0.065 | 40 | 29 | 310-749 | 41275
Incandescent 75W | 75 | 1200 | 75w incandescent to 23w CFL | 75w incandescent to 12w downlight fixture LED |  |  |  | I75 | 75 | 1 | [5 empty] | 0.075
Incandescent 100W | 100 | 1210 | 100w incandescent to 16w LED downlight screw base Lamp |  |  |  |  | I100 | 100 | 1 | [5 empty] | 0.1
Incandescent 150W | 150 | 1220 | 150w incandescent to 18w LED downlight screw base lamp |  |  |  |  | I150 | 150 | 1 | [5 empty] | 0.15
Incandescent 250W | 250 | 1230 | [5 empty] | I250 | 250 | 1 | [5 empty] | 0.25
Incandescent, 200W | 200 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | I200L/1 | I200/LL | 200 | 1
Incandescent 300W | 300 | 1240 | [5 empty] | I300 | 300 | 1 | [5 empty] | 0.3
Incandescent 500W | 500 | 1250 | [5 empty] | I500 | 500 | 1 | [5 empty] | 0.5
Incandescent 600W | 600 | 1260
Incandescent, (1) 40W ES lamp | 34 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | I40E/1 | I40/ES | 34 | 1
Incandescent, (1) 40W ES lamp | 34 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | I40EL/1 | I40/ES/LL | 34 | 1
Incandescent, (1) 60W ES lamp | 52 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | I60E/1 | I60/ES | 52 | 1
Incandescent, (1) 60W ES lamp | 52 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | I60EL/1 | I60/ES/LL | 52 | 1
Incandescent, (1) 75W ES lamp | 67 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | I75E/1 | I75/ES | 67 | 1
Incandescent, (1) 75W ES lamp | 67 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | I75EL/1 | I75/ES/LL | 67 | 1
Incandescent, (1) 100W ES lamp | 90 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | I100E/1 | I100/ES | 90 | 1
Incandescent, (1) 100W ES lamp | 90 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | I100EL/1 | I100/ES/LL | 90 | 1
Incandescent, (1) 150W ES lamp | 135 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | I150E/1 | I150/ES | 135 | 1
Incandescent, (1) 150W ES lamp | 135 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | I150EL/1 | I150/ES/LL | 135 | 1
Halogen, 20W MR16 | 20 | 1140 | 20w MR16 to 3w LED MR16 pin-based lamp
Halogen, 30W MR16 | 30 | 1150 | 30w MR16 to 5w LED MR16 pin-based lamp
Halogen, 50W MR16 | 50 | 1160 | [5 empty] | H50/LV | 50 | 1 | Halogen, (1) Low Voltage MR16 lamp |  |  |  |  | 0.06
HPS | Total | [5 empty] | SPC Reference Codes
Lamp Name | Watts | Lamp Number | Retrofit1 | Retrofit2 | Retrofit3 | Notes | FIXT CODE | LAMP CODE | NOM. W/LAMP | LAMP/ FIXT | DESCRIPTION | Lamp | Ballast Type2 | Output | Ballast Wiring | kW/ FIXT
High Pressure Sodium, (1) 35W lamp | 47 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | HPS35/1 | HPS35 | 35 | 1
High Pressure Sodium, (1) 50W lamp | 66 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | HPS50/1 | HPS50 | 50 | 1
High Pressure Sodium, (1) 70W lamp | 91 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | HPS70/1 | HPS70 | 70 | 1
High Pressure Sodium, (1) 100W lamp | 128 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | HPS100/1 | HPS100 | 100 | 1
High Pressure Sodium, (1) 150W lamp | 188 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | HPS150/1 | HPS150 | 150 | 1
High Pressure Sodium, (1) 200W lamp | 230 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | HPS200/1 | HPS200 | 200 | 1
High Pressure Sodium, (1) 250W lamp | 295 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | HPS250/1 | HPS250 | 250 | 1
High Pressure Sodium, (1) 310W lamp | 355 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | HPS310/1 | HPS310 | 310 | 1
High Pressure Sodium, (1) 360W lamp | 414 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | HPS360/1 | HPS360 | 360 | 1
High Pressure Sodium, (1) 400W lamp | 464 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | HPS400/1 | HPS400 | 400 | 1
High Pressure Sodium, (1) 750W lamp | 830 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | HPS750/1 | HPS750 | 750 | 1
High Pressure Sodium, (1) 1000W lamp | 1100 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | HPS1000/1 | HPS1000 | 1000 | 1
MH | Total | [5 empty] | SPC Reference Codes
Lamp Name | Watts | Lamp Number | Retrofit1 | Retrofit2 | Retrofit3 | Notes | FIXT CODE | LAMP CODE | BALLAST | NOM WATT/LAMP | LAMPER PER FIXT | Lamp | Ballast Type2 | Output | Ballast Wiring | kW/ FIXT
Metal halide, (1) 20W lamp, electronic ballast | 24 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | MH20L/1 | MH20 | Electronic | 20 | 1
Metal halide, (1) 22W lamp, electronic ballast | 26 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | MH22L/1 | MH22 | Electronic | 22 | 1
Metal halide, (1) 39W lamp, electronic ballast | 45 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | MH39L/1 | MH39 | Electronic | 39 | 1
Metal halide, (2) 39W lamp, electronic ballast | 89 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | MH39L/2 | MH39 | Electronic | 39 | 2
Metal halide, (1) 50W lamp, electronic ballast | 56 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | MH50L/1 | MH50 | Electronic | 50 | 1
Metal halide, (1) 70W lamp, electronic ballast | 80 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | MH70L/1 | MH70 | Electronic | 70 | 1
Metal halide, (1) 100W lamp, electronic ballast | 110 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | MH100L/1 | MH100 | Electronic | 100 | 1
Metal halide, (1) 150W lamp, electronic ballast | 168 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | MH150L/1 | MH150 | Electronic | 150 | 1
Metal halide, (1) 175W lamp, electronic ballast | 194 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | MH175L/1 | MH175 | Electronic | 175 | 1
Metal halide, (1) 200W lamp, prem. electronic ballast | 215 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | MH200LE/1 | MH200 | Elec-Prem | 200 | 1
Metal halide, (1) 250W lamp, prem. electronic ballast | 267 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | MH250LE/1 | MH250 | Elec-Prem | 250 | 1
Metal halide, (1) 320W lamp, prem. electronic ballast | 343 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | MH320LE/1 | MH320 | Elec-Prem | 320 | 1
Metal halide, (1) 350W lamp, prem. electronic ballast | 374 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | MH350LE/1 | MH350 | Elec-Prem | 350 | 1
Metal halide, (1) 400W lamp, prem. electronic ballast | 428 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | MH400LE/1 | MH400 | Elec-Prem | 400 | 1
Metal halide, (1) 32W lamp, mag ballast | 43 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | MH32/1 | MH32 | Magnetic | 32 | 1
Metal halide, (1) 50W lamp, mag ballast | 61 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | MH50/1 | MH50 | Magnetic | 50 | 1
Metal halide, (1) 70W lamp, mag ballast | 88 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | MH70/1 | MH70 | Magnetic | 70 | 1
Metal halide, (1) 100W lamp, mag ballast | 128 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | MH100/1 | MH100 | Magnetic | 100 | 1
Metal halide, (1) 150W lamp, mag ballast | 190 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | MH150/1 | MH150 | Magnetic | 150 | 1
Metal halide, (1) 175W lamp, mag ballast | 210 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | MH175/1 | MH175 | Magnetic | 175 | 1
Metal halide, (1) 250W lamp, mag ballast | 294 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | MH250/1 | MH250 | Magnetic | 250 | 1
Metal halide, (1) 400W lamp, mag ballast | 458 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | MH400/1 | MH400 | Magnetic | 400 | 1
Metal halide, (2) 400W lamp, mag ballast | 916 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | MH400/2 | MH400 | Magnetic | 400 | 2
Metal halide, (1) 750W lamp, mag ballast | 850 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | MH750/1 | MH750 | Magnetic | 750 | 1
Metal halide, (1) 1000W lamp, mag ballast | 1080 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | MH1000/1 | MH1000 | Magnetic | 1000 | 1
Metal halide, (1) 1500W lamp, mag ballast | 1605 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | MH1500/1 | MH1500 | Magnetic | 1500 | 1
Fluorescent | Total | [5 empty] | SPC Reference Codes
Lamp Name | Watts | Lamp Number | Retrofit1 | Retrofit2 | Retrofit3 | Notes | LAMP CODE | BALLAST TYPE | NOM. W/LAMP | LAMP/ FIXT | DESCRIPTION | Lamp | Ballast Type2 | Output | Ballast Wiring | kW/ FIXT
U-Tube, ES lamp, EEMB | 43 | 1500 |  |  |  |  | FU40T12/ES | Mag-ES | 35 | 1 | Fluorescent, (1) U-Tube, ES lamp |  |  |  |  | 0.043
U-Tube, T8 lamp | 31 | 1510 |  |  |  |  | FU31T8/6 | Electronic | 32 | 1 | Fluorescent, (1) U-Tube, T-8 lamp, Instant Start ballast |  |  |  |  | 0.031
U-Tube, (2) lamps | 59 | 1520
U-Tube, (2) ES lamps, EEMB | 72 | 1530 |  |  |  |  | FU40T12/ES | Mag-ES | 35 | 2 | Fluorescent, (2) U-Tube, ES lamp |  |  |  |  | 0.072
U-Tube, (2) T8 lamps | 58 | 1540 |  |  |  |  | FU31T8/6 | Electronic | 32 | 2 | Fluorescent, (2) U-Tube, T-8 lamp, Instand Start Ballast |  |  |  |  | 0.059
Circular lamp, 6" dia | 25 | 1550 |  |  |  |  | FC6T9 | Mag-STD | 20 | 1 | Fluorescent, (1) 6 circular lamp |  | RS ballast " |  |  | 0.025
Circular lamp, 8" dia | 26 | 1560 |  |  |  |  | FC8T9 | Mag-STD | 22 | 1 | Fluorescent, (1) 8 circular lamp |  | RS ballast " |  |  | 0.026
Circular lamp, 12" dia | 32 | 1570 |  |  |  |  | FC12T9 | Mag-STD | 32 | 1 | Fluorescent, (1) 12 circular lamp |  | RS ballast " |  |  | 0.031
Circular lamp, 16" dia | 40 | 1580 |  |  |  |  | FC16T9 | Mag-STD | 40 | 1 | Fluorescent, (1) 16 circular lamp " |  |  |  |  | 0.035
Circular lamp, 20W | 20 | 1590 |  |  |  |  | FC6T9 | Mag-STD | 20 | 1 | Fluorescent, Circlite, (1) 20W lamp, Preheat ballast |  |  |  |  | 0.02
Circular lamp, 22W | 22 | 1600 |  |  |  |  | FC8T9 | Mag-STD | 22 | 1 | Fluorescent, Circlite, (1) 22W lamp, preheat ballast |  |  |  |  | 0.02
Circular lamp, 32W | 40 | 1610 |  |  |  |  | FC12T9 | Mag-STD | 32 | 1 | Fluorescent, Circline, (1) 32W lamp, preheat ballast |  |  |  |  | 0.04
Exit_Sign | Total | [5 empty] | SPC Reference Codes
Lamp Name | Watts | Lamp Number | Retrofit1 | Retrofit2 | Retrofit3 | Notes | FIXTURE CODE | LAMP CODE | BALLAST | NOM W/LAMP | LAMPS PER FIXT | Lamp | Ballast Type2 | Output | Ballast Wiring | kW/ FIXT
Exit Sign, LED, (1) 2W , single sided | 6 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | ELED2/1 | LED2W |  | 2 | 1
Exit Sign, LED, (2) 2W , dual sided | 9 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | ELED2/2 | LED2W |  | 2 | 2
Exit Sign, compact fluorescent, (1) 5W | 9 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | ECF5/1 | CFT5W | Mag-STD | 5 | 1
Exit Sign, compact fluorescent, (2) 5W | 20 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | ECF5/2 | CFT5W | Mag-STD | 5 | 2
Exit Sign, compact fluorescent, (1) 7W | 10 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | ECF7/1 | CFT7W | Mag-STD | 7 | 1
Exit Sign, compact fluorescent, (2) 7W | 21 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | ECF7/2 | CFT7W | Mag-STD | 7 | 2
Exit Sign, compact fluorescent, (2) 9W | 20 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | ECF9/2 | CFT9W | Mag-STD | 9 | 2
Exit Sign, compact fluorescent, (1) 9W | 12 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | ECF9/1 | CFT9W | Mag-STD | 9 | 1
Exit Sign, T5 fluorescent, (1) 8W | 12 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | ECF8/1 | F8T5 | Mag-STD | 8 | 1
Exit Sign, T5 fluorescent, (2) 8W | 24 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | ECF8/2 | F8T5 | Mag-STD | 8 | 2
Exit Sign, incandescent, (1) 5W | 5 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | EI5/1 | I5 |  | 5 | 1
Exit Sign, incandescent, (2) 5W | 10 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | EI5/2 | I5 |  | 5 | 2
Exit Sign, incandescent, (2) 10W | 20 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | EI10/2 | I10 |  | 10 | 2
Exit Sign, incandescent, (1) 15W | 15 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | EI15/1 | I15 |  | 15 | 1
Exit Sign, incandescent, (2) 15W | 30 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | EI15/2 | I15 |  | 15 | 2
Exit Sign, incandescent, (1) 20W | 20 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | EI20/1 | I20 |  | 20 | 1
Exit Sign, incandescent, (2) 20W | 40 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | EI20/2 | I20 |  | 20 | 2
Exit Sign, incandescent, (1) 25W | 25 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | EI25/1 | I25 |  | 25 | 1
Exit Sign, incandescent, (2) 25W | 50 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | EI25/2 | I25 |  | 25 | 2
Exit Sign, incandescent, (1) 34W | 34 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | EI34/1 | I34 |  | 34 | 1
Exit Sign, incandescent, (2) 34W | 68 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | EI34/2 | I34 |  | 34 | 2
Exit Sign, incandescent, (1) 40W | 40 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | EI40/1 | I40 |  | 40 | 1
Exit Sign, incandescent, (2) 40W | 80 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | EI40/2 | I40 |  | 40 | 2
Exit Sign, incandescent, (2) 50W | 100 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | EI50/2 | I50 |  | 50 | 2
Exit Sign, tungsten, (1) 7.5 W | 8 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | EI7.5/1 | I7.5 |  | 7.5 | 1
Exit Sign, tungsten, (2) 7.5 W | 15 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | EI7.5/2 | I7.5 |  | 7.5 | 2
Misc | Total | [5 empty] | SPC Reference Codes
Lamp Name | Watts | Lamp Number | Retrofit1 | Retrofit2 | Retrofit3 | Notes | FIXT CODE | LAMP CODE | BALLAST TYPE | NOM. W/LAMP | LAMP/ FIXT | Lamp | Ballast Type2 | Output | Ballast Wiring | kW/ FIXT
Low pressure sodium 35w | 50 | 1810
Low pressure sodium 90w | 115 | 1820
Mercury vapor, (1) 40W lamp | 50 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | MV40/1 | MV40 |  | 40 | 1
Mercury vapor, (1) 50W lamp | 74 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | MV50/1 | MV50 |  | 50 | 1
Mercury vapor, (1) 75W lamp | 93 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | MV75/1 | MV75 |  | 75 | 1
Mercury vapor, (1) 100W lamp | 125 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | MV100/1 | MV100 |  | 100 | 1
Mercury vapor, (1) 175W lamp | 205 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | MV175/1 | MV175 |  | 175 | 1
Mercury vapor, (1) 250W lamp | 290 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | MV250/1 | MV250 |  | 250 | 1
Mercury vapor, (1) 400W lamp | 455 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | MV400/1 | MV400 |  | 400 | 1
Mercury vapor, (2) 400W lamp | 910 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | MV400/2 | MV400 |  | 400 | 2
Mercury vapor, (1) 700W lamp | 780 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | MV700/1 | MV700 |  | 700 | 1
Mercury vapor, (1) 1000W lamp | 1080 |  | Statewide Customized Offering Manual Appendix B | Revised January 2012 | http://www.aesc-inc.com/download/spc/2012SPCDocs/UnifiedManual/App%20B%20Standard%20Fixture%20Watts.pdf |  | MV1000/1 | MV1000 |  | 1000 | 1
Neon 6' | 69 | 1850 |  |  |  | 11.5 W/ft "Internally Illuminated Signs – Proposed Channel Letter & Box Sign, System Efficacy Standards" PGE, 3/25/02 per http://www.energy.ca.gov/outdoor_lighting/documents/public_comments/2002-03-26_illum_sign.doc
Neon 7400w | 7400 | 1860 |  |  |  | Grainger 389 p. 1048
Neon 8' | 92 | 1870 |  |  |  | 11.5 W/ft "Internally Illuminated Signs – Proposed Channel Letter & Box Sign, System Efficacy Standards" PGE, 3/25/02 per http://www.energy.ca.gov/outdoor_lighting/documents/public_comments/2002-03-26_illum_sign.doc
Fiber optic display lighting unit | 95 | 1800 |  |  |  | 70 watt MH
Induction 40w | 44 | 1830 | [7 empty] | 40 | 1 | Sylvania ICE40/RCT/2P/ECO
Induction 70w | 79 | 1832 | [7 empty] | 70 | 1 | Sylvania ICE70/2P/ECO
Induction 80w | 87 | 1833 | [7 empty] | 80 | 1 | Maxlite MLSM80IND50
Induction 100w | 106 | 1834 | [7 empty] | 100 | 1 | Sylvania ICE100/2P/ECO
Induction 120w | 128 | 1836 | [7 empty] | 120 | 1
Induction 150w | 161 | 1838 | [7 empty] | 150 | 1 | Sylvania ICE150/2P/ECO
Induction 200w | 215 | 1839 | [7 empty] | 200 | 1 | Sylvania ICE200/RCT/2P/ECO
LED | Total | [5 empty] | SPC Reference Codes
Lamp Name | Watts | Lamp Number | Retrofit1 | Retrofit2 | Retrofit3 | Notes | LAMP CODE | BALLAST TYPE | NOM. W/LAMP | LAMP/ FIXT | DESCRIPTION | Lamp | Ballast Type2 | Output | Ballast Wiring | kW/ FIXT
LED, outdoor pole/arm mounted, 42W | 42 | 1000 |  |  |  | Source: Efficiency Maine |  |  |  |  | Sensity Systems Roadway Luminaire, Citadel Series, Drive current 700mA, 1 module
LED, outdoor pole/arm mounted, 58W | 58 | 1001 | #REF! | [7 empty] | Sensity Systems Roadway Luminaire, Citadel Series, Drive current 1000mA, 1 module
LED, outdoor pole/arm mounted, 83W | 83 | 1002 |  |  |  | Source: Efficiency Maine |  |  |  |  | Sensity Systems Roadway Luminaire, Citadel Series, Drive current 700mA, 2 modules
LED, outdoor pole/arm mounted, 116W | 116 | 1003 | #REF! | [7 empty] | Sensity Systems Roadway Luminaire, Citadel Series, Drive current 1000mA, 2 modules
LED, outdoor pole/arm mounted, 125W | 125 | 1004 |  |  |  | Source: Efficiency Maine |  |  |  |  | Sensity Systems Roadway Luminaire, Citadel Series, Drive current 700mA, 3 modules
LED, outdoor pole/arm mounted, 174W | 174 | 1005 | #REF! | [7 empty] | Sensity Systems Roadway Luminaire, Citadel Series, Drive current 1000mA, 3 modules
LED, outdoor pole/arm mounted, 168W | 168 | 1006 |  |  |  | Source: Efficiency Maine |  |  |  |  | Sensity Systems Roadway Luminaire, Citadel Series, Drive current 700mA, 4 modules
LED, outdoor pole/arm mounted, 235W | 235 | 1007 | #REF! | [7 empty] | Sensity Systems Roadway Luminaire, Citadel Series, Drive current 1000mA, 4 modules
LED, wallpack, 30W | 30 | 1008 |  |  |  | Source: Efficiency Maine |  |  |  |  | RAB lighting WPLED26N
LED, wallpack, 60W | 60 | 1009 |  |  |  | Source: Efficiency Maine |  |  |  |  | RAB lighting WPLED52N
LED, wallpack, 82W | 82 | 1010 |  |  |  | Source: Efficiency Maine |  |  |  |  | RAB lighting WPLED80N/PCS
LED, wallpack, 112W | 112 | 1011 |  |  |  | Source: Efficiency Maine |  |  |  |  | RAB lighting WPLED104N
LED, parking garage, 43W | 43 | 1012 |  |  |  | Source: Efficiency Maine |  |  |  |  | Sensity Systems Garage Canopy Luminaire, 1 module
LED, parking garage, 85W | 85 | 1013 |  |  |  | Source: Efficiency Maine |  |  |  |  | Sensity Systems Garage Canopy Luminaire, 2 compact modules
LED, parking garage, 123W | 123 | 1014 |  |  |  | Source: Efficiency Maine
LED, downlight fixture, 9W | 9 | 1015 |  |  |  | Source: Efficiency Maine
LED, downlight fixture, 10W | 10 | 1016 | #REF!
LED, downlight fixture, 12W | 12 | 1017 |  |  |  | Source: Efficiency Maine
LED, downlight fixture, 15W | 15 | 1018 |  |  |  | Source: Efficiency Maine
LED, downlight plug in lamp, 13W | 13 | 1019 | #REF! | [7 empty] | Lunera Helen Lamp
LED, downlight screw in lamp, 5W | 5 | 1020 |  |  |  | Source: Efficiency Maine
LED, downlight screw in lamp, 7W | 7 | 1021 |  |  |  | Source: Efficiency Maine
LED, downlight screw in lamp, 9W | 9 | 1022 | #REF!
LED, downlight screw in lamp, 11W | 11 | 1023 |  |  |  | Source: Efficiency Maine
LED, downlight screw in lamp, 13W | 13 | 1024 |  |  |  | Source: Efficiency Maine
LED, downlight screw in lamp, 15W | 15 | 1025 |  |  |  | Source: Efficiency Maine
LED, downlight screw in lamp, 18W | 18 | 1026 |  |  |  | Source: Efficiency Maine
LED, refrigerated display case, end-mount, 6W | 6 | 1027 |  |  |  | Source: Efficiency Maine |  |  |  |  | Philips PrimeSet RDL500 side mount, 59"
LED, refrigerated display case, end-mount, 9W | 9 | 1028 |  |  |  | Source: Efficiency Maine |  |  |  |  | Osram Sylvania LEDstixx LSX/V/3/S/24V/850/72/R, 6'
LED, refrigerated display case, center-mount, 12W | 12 | 1029 |  |  |  | Source: Efficiency Maine |  |  |  |  | Philips PrimeSet RDL500 center mount, 59"
LED, refrigerated display case, center-mount, 17W | 17 | 1030 |  |  |  | Source: Efficiency Maine |  |  |  |  | Osram Sylvania LEDstixx LSX/V/3/S/24V/850/72/C, 6'
LED, MR16 pin-based lamp, 3W | 3 | 1031 | #REF!
LED, MR16 pin-based lamp, 4W | 4 | 1032 | #REF!
LED, MR16 pin-based lamp, 5W | 5 | 1033 | #REF!
LED, MR16 pin-based lamp, 7W | 6 | 1034 | #REF!
LED, MR16 pin-based lamp, 6W | 7 | 1035 | #REF!
LED, MR16 pin-based lamp, 10W | 10 | 1036 | #REF!

## Space use type data
Space Use Type Table |  |  |  | Note: only the space use types in blue are used in Project Input Table | [5 empty] | 2016 Title 24 Lighting Power Allowance Tables
LPA Source: 2016 Title 24 | [12 empty] | Color cells Indicate the Allowed Lighting Power differs from 2013 Title 24
Note: shaded cells in watts/sf column indicate updated lighting power allowances per the 2016 code update
watts/sf
Space end use type | Bldg type for HVAC IE and CDF factors | Whole Bldg | Area Category | Lookup Value used in lighting calc | Hours | Occupancy sensor | Photocontrol (daylight ctrl) | Combination OC/photocontrol | Manual bi-level switch | TABLE 140.6-B COMPLETE BUILDING METHOD LIGHTING POWER DENSITY VALUES |  |  |  | ALLOWED LIGHTING POWER (W/ft²) |  |  |  | ALLOWED LIGHTING POWER (W/ft²)
All others | Small Office | 0.5 | 0.5 | 0.5 | 2590 | 7% | 18% | 34% | 6% |  | ALLOWED LIGHTING POWER DENSITY (WATTS PER SQUARE FOOT)
Assembly | Assembly | 1.4 | 1.4 | 1.4 | 2610 | 36% | 0% | 0% | 6% | TYPE OF BUILDING |  | PRIMARY FUNCTION AREA |  |  | PRIMARY FUNCTION AREA
Auto repair | Light Industrial Manuf. |  | 0.9 | 0.9 | 3220 | 7% | 0% | 0% | 6% | Auditorium Building | 1.4 | Auditorium Area |  | 1.4 3 | Library Area |  | Reading areas | 1.1 3
Beauty Salon | Small Retail |  | 1.7 | 1.7 | 2610 | 15% | 29% | 34% | 6% | Classroom Building | 1.1 | Auto Repair Area |  | 0.9 2 |  |  | Stack areas | 1.5 3
Civic meeting place | Assembly |  | 1.3 | 1.3 | 2610 | 36% | 36% | 40% | 6% | Commercial and Industrial Storage Building | 0.6 | Beauty Salon Area |  | 1.7 | Lobby Area |  | Hotel lobby | 0.95 13
Classroom, whole bldg | Primary School | 0.95 |  | 0.95 | 2420 | 18% | 29% | 34% | 6% | Convention Center Building | 1 | Civic Meeting Place Area |  | 1.3 3 |  |  | Main entry lobby | 0.95 13
School - University | University | 0.95 | 1.2 | 1.2 | 2420 | 18% | 29% | 34% | 6% | Financial Institution Building | 1 | Classroom, Lecture, Training, Vocational |  |  | Locker/Dressing Room
Refrigerated space | Refrigerated Warehouse | 0.6 | 0.7 | 0.7 | 3420 | 31% | 28% | 40% | 6% | General Commercial Building/Industrial Work Building | 1 | Areas |  | 1.2 5 |  |  |  | 0.7
Storage with htg or clg | Conditioned Storage |  | 0.6 | 0.6 | 3420 | 31% | 28% | 40% | 6% | Grocery Store Building | 1.5 | Commercial and Industrial Storage Areas |  |  | Lounge Area
Commercial and industrial storage-whole bldg | Conditioned Storage | 0.6 |  | 0.6 | 3420 | 31% | 28% | 40% | 6% | Library Building | 1.2 | (conditioned and unconditioned) |  | 0.6 |  |  |  | 0.9 3
Convention centers-whole building | Assembly | 1.2 |  | 1.2 | 2610 | 36% | 0% | 0% | 0% | Medical Building/Clinic Building | 1 | Commercial and Industrial Storage Areas |  |  | Malls and Atria
Convention, conference, multipurpose, meeting centers | Assembly |  | 1.2 | 1.2 | 2610 | 36% | 29% | 40% | 35% | Office Building | 0.8 | (refrigerated) |  | 0.7 |  |  |  | 0.95 3
Corridors, restrooms, stairs, support areas | Large Office |  | 0.6 | 0.6 | 2640 | 15% | 15% | 0% | 0% | Parking Garage Building | 0.2 | Convention, Conference, Multipurpose and Meeting Center Areas |  |  | Medical and Clinical Care Area
Restaurant | Sit-Down Restaurant |  | 1.1 | 1.1 | 4830 | 35% | 18% | 40% | 6% | Religious Facility Building | 1.5 | [6 empty] | 1.2
Restroom/hallway/small storage | Unconditioned Storage |  | 0.6 | 0.6 | 500 | 7% | 0% | 0% | 0% | Restaurant Building | 1.1 |  |  | 1.2 3
Exercise center, gymnasium | Assembly |  | 1 | 1 | 3380 | 7% | 36% | 0% | 6% | School Building | 0.95 | Corridor, Restroom, Stair, and Support |  |  | Office Area | > 250 square feet
Exhibit, museum | Assembly |  | 1.8 | 1.8 | 2610 | 7% | 0% | 0% | 0% | Theater Building | 1.3 | Areas |  | 0.6 |  |  |  | 0.75
Exterior | Exterior |  |  | 0 | 4180 | 17% | 17% | 17% | 0% | All others buildings | 0.5 | Dining Area |  | 1.0 3 |  | ≤ 250 square feet |  | 1
Financial institutions-whole bldg | Large Office | 1 |  | 1 | 2590 | 22% | 27% | 40% | 35% |  |  | Electrical, Mechanical, Telephone |  |  | Parking Garage Area | Parking Area
Financial transactions | Large Office |  | 1 | 1 | 2590 | 22% | 27% | 40% | 35% |  |  | Rooms |  | 0.55 2 |  |  |  | 0.14
Manufacturing | Light Industrial Manuf. |  | 1 | 1 | 3220 | 45% | 0% | 0% | 0% |  |  | Exercise Center, Gymnasium Areas |  | 1 |  | Dedicated Ramps |  | 0.3
General comm & ind. work-low bay | Light Industrial Manuf. |  | 0.9 | 0.9 | 3220 | 45% | 0% | 0% | 0% |  |  | Exhibit, Museum Areas |  |  |  | Daylight Adaptation
General comm & ind. work-precision | Light Industrial Manuf. |  | 1.2 | 1.2 | 3220 | 45% | 0% | 0% | 0% |  |  |  |  | 1.8 |  | Zones 9 |  | 0.6
General comm & ind. work-whole building | Light Industrial Manuf. | 1 |  | 1 | 3220 | 45% | 0% | 40% | 0% |  |  | Financial Transaction Area |  | 1.0 3 | Religious Worship Area |  |  | 1.5 3
Grocery sales area | Grocery |  | 1.2 | 1.2 | 4910 | 45% | 36% | 0% | 0% |  |  | General Commercial and Industrial Work Areas | Low bay |  | Retail Merchandise Sales, Wholesale
Grocery | Grocery | 1.5 |  | 1.5 | 4910 | 15% | 36% | 0% | 0% |  |  |  |  | 0.9 2 | Showroom Areas |  |  | 1.2 6 and 7
Hotel function areas | Hotel |  | 1.4 | 1.4 | 1950 | 7% | 18% | 34% | 0% |  |  |  | High bay | 1.0 2
Hotel, lobby | Hotel |  | 0.95 | 0.95 | 5260 | 7% | 18% | 34% | 0% |  |  |  | Precision | 1.2 4 | Theater Area |  | Motion picture | 0.9 3
Hotel | Hotel | 1.4 |  | 1.4 | 1950 | 7% | 18% | 34% | 0% |  |  | Grocery Sales Area |  | 1.2 6 and 7 |  |  | Performance | 1.4 3
Motel | Motel |  | 1 | 1 | 4160 | 7% | 18% | 34% | 0% |  |  | Hotel Function Area |  | 1.4 3 | Transportation Function Area | Concourse & Baggage |  | 0.5
Nursing home | Motel |  | 1.5 | 1.5 | 4160 | 7% | 18% | 34% | 0% | [6 empty] | Ticketing |  | 1
Kitchen, food preparation | Sit-Down Restaurant |  | 1.2 | 1.2 | 4830 | 30% | 0% | 0% | 0% |  |  | Kitchen, Food Preparation Areas |  | 1.2 | Videoconferencing Studio |  |  | 1.2 8
Manufacturing - hi-tech | Bio/Tech Manuf. |  | 1.4 | 1.4 | 3530 | 7% | 0% | 0% | 0% |  |  | Laboratory Area, Scientific |  | 1.4 1 | Waiting Area |  |  | 0.8 3
Storage without htg or clg | Unconditioned Storage |  | 0.6 | 0.6 | 3380 | 15% | 0% | 0% | 0% |  |  | Laundry Area |  | 0.7 | All other areas |  |  | 0.5
Library, reading area | Small Office | 1.3 | 1.1 | 1.1 | 2610 | 15% | 29% | 34% | 0%
Library, stacks | Small Office |  | 1.5 | 1.5 | 2610 | 15% | 29% | 34% | 0%
Library, whole bldg | Small Office | 1.2 |  | 1.2 | 2610 | 15% | 29% | 34% | 0%
Lobbies | Large Office |  | 0.95 | 0.95 | 2640 | 7% | 18% | 34% | 0%
Locker/dressing room | Unconditioned Storage |  | 0.8 | 0.8 | 2610 | 7% | 0% | 0% | 0%
Lounge/recreation | Assembly |  | 0.9 | 0.9 | 2610 | 30% | 18% | 34% | 6%
Malls and atrias | Assembly |  | 0.95 | 0.95 | 3380 | 22% | 27% | 34% | 0%
Hospital | Large Office | 1 |  | 1 | 5260 | 22% | 27% | 34% | 0%
Medical and clinical care areas | Large Office |  | 1.2 | 1.2 | 5260 | 22% | 18% | 34% | 6%
Office space < 250 sf | Small Office |  | 1 | 1 | 2640 | 22% | 27% | 40% | 35%
Office | Large Office | 0.8 | 0.8 | 0.8 | 2640 | 22% | 27% | 40% | 35%
Office space, multipurpose <1,000 sf | Small Office |  |  | 0.75 | 2640 | 22% | 27% | 40% | 35%
Office space, conference room | Small Office |  |  | 0.75 | 2640 | 22% | 27% | 40% | 35%
Office, whole bldg | Large Office | 0.8 |  | 0.8 | 2640 | 22% | 27% | 0% | 0%
Parking - ramps, exits | Unconditioned Storage |  | 0.3 | 0.3 | 4100 | 15% | 18% | 40% | 0%
Parking garage, parking area | Unconditioned Storage |  | 0.14 | 0.14 | 4100 | 15% | 18% | 40% | 0%
Outdoor lighting | Unconditioned Storage | 0.3 |  | 0.3 | 4180 | 17% | 17% | 17% | 0%
Parking garage, whole bldg | Unconditioned Storage | 0.2 |  | 0.2 | 2610 | 15% | 18% | 40% | 0%
Refrigerated display case (grocery) | Refrigerated Warehouse |  |  | 0 | 4910 | 35% | 0% | 0% | 0%
Religious facility, whole bldg | Assembly | 1.5 |  | 1.5 | 2610 | 7% | 18% | 34% | 35%
Religious, worship areas | Assembly |  | 1.5 | 1.5 | 2610 | 7% | 18% | 34% | 35%
Retail and wholesale stores | Department Store | 1.2 |  | 1.2 | 3380 | 15% | 36% | 40% | 6%
Retail | Small Retail |  | 1.2 | 1.2 | 3380 | 15% | 36% | 40% | 6%
School | Primary School | 1 |  | 1 | 2280 | 29% | 29% | 34% | 6%
Tenant lease space | Small Office |  | 1 | 1 | 3380 | 7% | 18% | 34% | 35%
Theater, whole bldg | Assembly | 1.3 |  | 1.3 | 2610 | NA | 0% | 0% | 0%
Theaters, motion picture | Assembly |  | 0.9 | 0.9 | 2610 | NA | 0% | 0% | 0%
Theaters, performance | Assembly |  | 1.4 | 1.4 | 2610 | NA | 0% | 0% | 0%
Transportation function area | Light Industrial Manuf. |  | 1 | 1 | 5260 | NA | 18% | 34% | 6%
Other | Light Industrial Manuf. |  | 0.5 | 0.5 | 1200 | NA | 0% | 0% | 0%
Waiting area | Large Office |  | 0.8 | 0.8 | 2610 | 7% | 18% | 34% | 6%

## Lookup tables
Range_name | climate_zone | E_contrl_type | LT |  | N_ctrl_type | IE_table
| CZ01 | None | LED |  | Occupancy sensor | HVAC Interactive Effects-Non CFL |  |  | note: Non-CFL IE effects used in calculator (below CFL effects table values are for reference only)
| CZ02 | Manual | T8_HP_4ft |  | Photocontrol (daylight ctrl) |  | CZ01 |  | CZ02 |  | CZ03 |  | CZ04 |  | CZ05 |  | CZ06 |  | CZ07 |  | CZ08 |  | CZ09 |  | CZ10 |  | CZ11 |  | CZ12 |  | CZ13 |  | CZ14 |  | CZ15 |  | CZ16
| CZ03 | Time clock | T8_4ft |  | Combination OC/photocontrol | Building Type | Energy_CZ01 | Demand_CZ01 | Energy_CZ02 | Demand_CZ02 | Energy_CZ03 | Demand_CZ03 | Energy_CZ04 | Demand_CZ04 | Energy_CZ05 | Demand_CZ05 | Energy_CZ06 | Demand_CZ06 | Energy_CZ07 | Demand_CZ07 | Energy_CZ08 | Demand_CZ08 | Energy_CZ09 | Demand_CZ09 | Energy_CZ10 | Demand_CZ10 | Energy_CZ11 | Demand_CZ11 | Energy_CZ12 | Demand_CZ12 | Energy_CZ13 | Demand_CZ13 | Energy_CZ14 | Demand_CZ14 | Energy_CZ15 | Demand_CZ15 | Energy_CZ16 | Demand_CZ16
| CZ04 | Automated control | T8_all_other_lengths |  | User-defined savings | Assembly | 0.95 | 0.97 | 1.03 | 1.18 | 1.02 | 1.18 | 1.05 | 1.18 | 1.03 | 1.17 | 1.12 | 1.27 | 1.1 | 1.22 | 1.13 | 1.23 | 1.12 | 1.26 | 1.09 | 1.22 | 1.05 | 1.18 | 1.04 | 1.18 | 1.05 | 1.22 | 1.07 | 1.14 | 1.19 | 1.2 | 0.99 | 1.19
| CZ05 | Manual bi-level switch | CFL |  | Same as pre-existing | Primary School | 0.99 | 1.09 | 1.06 | 1 | 1.07 | 1 | 1.08 | 1.62 | 1.06 | 1.23 | 1.16 | 1.58 | 1.14 | 1.29 | 1.18 | 1.34 | 1.16 | 1.86 | 1.13 | 1.88 | 1.06 | 1 | 1.07 | 1 | 1.08 | 1 | 1.09 | 1.4 | 1.21 | 1.34 | 0.97 | 1
| CZ06 | Occupancy sensor | T5_Lamp |  |  | Secondary School | 0.97 | 1.03 | 1.04 | 1 | 1.04 | 1 | 1.07 | 1.32 | 1.04 | 1.22 | 1.14 | 1.43 | 1.12 | 1.26 | 1.16 | 1.31 | 1.15 | 1.84 | 1.12 | 1.77 | 1.07 | 1 | 1.06 | 1 | 1.08 | 1 | 1.09 | 1.47 | 1.21 | 1.3 | 0.98 | 1
| CZ07 | Unknown | T12_Lamp |  |  | Community College | 1.03 | 1.08 | 1.09 | 1.2 | 1.08 | 1.12 | 1.11 | 1.36 | 1.08 | 1.22 | 1.16 | 1.27 | 1.14 | 1.25 | 1.17 | 1.28 | 1.16 | 1.31 | 1.15 | 1.29 | 1.12 | 1.44 | 1.11 | 1.28 | 1.13 | 1.5 | 1.12 | 1.33 | 1.24 | 1.34 | 1.04 | 1.24
| CZ08 |  | Incandescent |  |  | University | 1.06 | 1.14 | 1.1 | 1.2 | 1.1 | 1.14 | 1.12 | 1.27 | 1.1 | 1.23 | 1.16 | 1.23 | 1.14 | 1.24 | 1.17 | 1.27 | 1.16 | 1.27 | 1.15 | 1.26 | 1.12 | 1.34 | 1.12 | 1.22 | 1.13 | 1.58 | 1.13 | 1.28 | 1.2 | 1.28 | 1.06 | 1.23
| CZ09 |  | HPS |  |  | Relocatable Classroom | 0.97 | 1.08 | 1.02 | 1 | 1 | 1 | 1.05 | 1.22 | 1.02 | 1.26 | 1.12 | 1.67 | 1.13 | 1.26 | 1.11 | 1.29 | 1.11 | 1.29 | 1.11 | 1.31 | 1.04 | 1 | 1.04 | 1 | 1.05 | 1 | 1.09 | 1.33 | 1.19 | 1.31 | 1 | 1
| CZ10 | OC_mandatory | MH |  |  | Grocery | 0.8 | 0.76 | 0.91 | 1.19 | 0.87 | 1.18 | 0.94 | 1.24 | 0.87 | 1.17 | 1.03 | 1.2 | 1 | 1.17 | 1.05 | 1.25 | 1.06 | 1.27 | 1.05 | 1.28 | 0.99 | 1.28 | 0.96 | 1.28 | 1 | 1.31 | 1.05 | 1.32 | 1.13 | 1.3 | 0.96 | 1.25
| CZ11 | Classroom, whole bldg | Fluorescent |  |  | Hospital | 1.07 | 1.11 | 1.1 | 1.19 | 1.11 | 1.16 | 1.11 | 1.22 | 1.09 | 1.19 | 1.16 | 1.26 | 1.15 | 1.23 | 1.17 | 1.26 | 1.17 | 1.28 | 1.14 | 1.27 | 1.11 | 1.23 | 1.11 | 1.23 | 1.12 | 1.27 | 1.13 | 1.28 | 1.19 | 1.29 | 1.06 | 1.23
| CZ12 | Classrooms, lecture, vocational, training | Exit_Sign |  |  | Nursing Home | 0.97 | 1.04 | 1.03 | 1.19 | 1.02 | 1.13 | 1.05 | 1.24 | 1.01 | 1.14 | 1.08 | 1.26 | 1.07 | 1.25 | 1.1 | 1.29 | 1.1 | 1.31 | 1.09 | 1.32 | 1.06 | 1.25 | 1.05 | 1.25 | 1.07 | 1.31 | 1.08 | 1.32 | 1.16 | 1.33 | 0.99 | 1.27
| CZ13 | Commercial and industrial refrigerated storage areas | Misc |  |  | Hotel | 0.88 | 1.1 | 0.97 | 1.23 | 0.98 | 1.2 | 1.01 | 1.24 | 0.97 | 1.21 | 1.09 | 1.27 | 1.1 | 1.24 | 1.11 | 1.28 | 1.1 | 1.29 | 1.07 | 1.29 | 1.02 | 1.25 | 1 | 1.25 | 1.03 | 1.29 | 1.03 | 1.3 | 1.16 | 1.29 | 0.9 | 1.27
| CZ14 | Commercial and industrial storage areas | User-defined |  |  | Motel | 0.95 | 1.17 | 1.02 | 1.21 | 1.03 | 1.19 | 1.05 | 1.22 | 1.02 | 1.2 | 1.13 | 1.26 | 1.14 | 1.24 | 1.15 | 1.27 | 1.14 | 1.3 | 1.12 | 1.3 | 1.05 | 1.23 | 1.04 | 1.23 | 1.07 | 1.3 | 1.08 | 1.32 | 1.2 | 1.32 | 0.96 | 1.25
| CZ15 | Commercial and industrial storage-whole bldg |  |  |  | Bio/Tech Manuf. | 1.08 | 1.11 | 1.11 | 1.19 | 1.12 | 1.14 | 1.12 | 1.15 | 1.11 | 1.18 | 1.18 | 1.21 | 1.17 | 1.23 | 1.18 | 1.26 | 1.18 | 1.26 | 1.14 | 1.26 | 1.12 | 1.34 | 1.11 | 1.2 | 1.12 | 1.56 | 1.14 | 1.23 | 1.19 | 1.26 | 1.07 | 1.21
| CZ16 | Convention, conference, multipurpose, meeting centers |  |  |  | Light Industrial Manuf. | 0.97 | 1.03 | 1.04 | 1.17 | 1.04 | 1.11 | 1.05 | 1.15 | 1.03 | 1.17 | 1.11 | 1.19 | 1.08 | 1.19 | 1.11 | 1.2 | 1.11 | 1.22 | 1.08 | 1.21 | 1.04 | 1.15 | 1.04 | 1.18 | 1.05 | 1.2 | 1.06 | 1.2 | 1.15 | 1.29 | 0.99 | 1.19
|  | Corridors, restrooms, stairs, support areas |  |  |  | Large Office | 1.08 | 1.16 | 1.11 | 1.26 | 1.11 | 1.16 | 1.12 | 1.28 | 1.1 | 1.23 | 1.17 | 1.3 | 1.16 | 1.27 | 1.18 | 1.33 | 1.17 | 1.33 | 1.17 | 1.32 | 1.13 | 1.29 | 1.12 | 1.31 | 1.14 | 1.33 | 1.16 | 1.31 | 1.23 | 1.32 | 1.08 | 1.29
|  | Exterior |  |  |  | Small Office | 1.01 | 1.11 | 1.05 | 1.2 | 1.05 | 1.13 | 1.07 | 1.24 | 1.06 | 1.19 | 1.15 | 1.28 | 1.16 | 1.25 | 1.16 | 1.28 | 1.15 | 1.32 | 1.13 | 1.29 | 1.07 | 1.28 | 1.07 | 1.23 | 1.07 | 1.34 | 1.11 | 1.3 | 1.21 | 1.3 | 1.01 | 1.27
|  | Library, stacks |  |  |  | Sit-Down Restaurant | 0.91 | 0.98 | 1.01 | 1.21 | 1 | 1.18 | 1.04 | 1.2 | 1 | 1.19 | 1.11 | 1.28 | 1.12 | 1.26 | 1.12 | 1.24 | 1.11 | 1.26 | 1.09 | 1.23 | 1.04 | 1.19 | 1.03 | 1.18 | 1.04 | 1.25 | 1.07 | 1.16 | 1.17 | 1.26 | 0.99 | 1.21
|  | Office space < 250 sf |  |  |  | Fast-Food Restaurant | 0.97 | 1.03 | 1.03 | 1.17 | 1.02 | 1.14 | 1.05 | 1.18 | 1.02 | 1.15 | 1.09 | 1.24 | 1.12 | 1.22 | 1.11 | 1.22 | 1.11 | 1.24 | 1.09 | 1.22 | 1.05 | 1.18 | 1.05 | 1.18 | 1.06 | 1.23 | 1.07 | 1.23 | 1.15 | 1.23 | 1 | 1.2
|  | Office space, multipurpose <1,000 sf |  |  |  | Department Store | 0.98 | 1.07 | 1.07 | 1.19 | 1.08 | 1.19 | 1.09 | 1.2 | 1.08 | 1.18 | 1.16 | 1.24 | 1.15 | 1.21 | 1.17 | 1.22 | 1.15 | 1.25 | 1.13 | 1.23 | 1.07 | 1.19 | 1.07 | 1.21 | 1.08 | 1.24 | 1.09 | 1.21 | 1.17 | 1.24 | 0.99 | 1.21
Replacement | Retrofit | Office space, conference room | Rebate levels | $/kWh |  | Big Box Retail | 0.97 | 1.07 | 1.06 | 1.19 | 1.06 | 1.19 | 1.08 | 1.2 | 1.06 | 1.19 | 1.15 | 1.25 | 1.14 | 1.22 | 1.15 | 1.24 | 1.14 | 1.27 | 1.12 | 1.25 | 1.06 | 1.2 | 1.06 | 1.2 | 1.07 | 1.26 | 1.09 | 1.26 | 1.17 | 1.26 | 0.98 | 1.21
A | M | Parking garage, parking area | Rebate1 | 0.15 |  | Small Retail | 0.98 | 1.09 | 1.06 | 1.18 | 1.06 | 1.17 | 1.08 | 1.19 | 1.06 | 1.17 | 1.14 | 1.23 | 1.13 | 1.21 | 1.15 | 1.23 | 1.14 | 1.26 | 1.12 | 1.24 | 1.06 | 1.19 | 1.06 | 1.2 | 1.07 | 1.25 | 1.09 | 1.2 | 1.17 | 1.24 | 0.99 | 1.21
B | N | Parking garage |  |  |  | Conditioned Storage | 0.84 | 0.89 | 0.95 | 1.21 | 0.92 | 1.01 | 0.98 | 1.26 | 0.91 | 1.15 | 1.03 | 1.32 | 1.01 | 1.27 | 1.05 | 1.32 | 1.04 | 1.34 | 1.04 | 1.31 | 0.98 | 1.21 | 0.98 | 1.25 | 0.99 | 1.29 | 1.01 | 1.29 | 1.11 | 1.3 | 0.91 | 1.27
C | O | Parking garage, whole bldg |  |  |  | Unconditioned Storage | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
D | P |  |  |  |  | Refrigerated Warehouse | 1.54 | 1.81 | 1.59 | 1.32 | 1.63 | 1.29 | 1.62 | 1.32 | 1.58 | 1.26 | 1.58 | 1.34 | 1.62 | 1.35 | 1.6 | 1.25 | 1.59 | 1.26 | 1.58 | 1.26 | 1.55 | 1.25 | 1.57 | 1.32 | 1.56 | 1.25 | 1.52 | 1.32 | 1.63 | 1.26 | 1.38 | 1.27
E | Q | Application |  |  |  | Exterior | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
F | R | General hardscape lighting
G | S | Outdoor sign |  |  |  | HVAC Interactive Effects-CFL
H | T | Building entrance or exit |  |  |  |  | CZ01 |  | CZ02 |  | CZ03 |  | CZ04 |  | CZ05 |  | CZ06 |  | CZ07 |  | CZ08 |  | CZ09 |  | CZ10 |  | CZ11 |  | CZ12 |  | CZ13 |  | CZ14 |  | CZ15 |  | CZ16
I | U | Primary entrance to senior care facility |  |  |  | Building Type | Energy_CZ01 | Demand_CZ01 | Energy_CZ02 | Demand_CZ02 | Energy_CZ03 | Demand_CZ03 | Energy_CZ04 | Demand_CZ04 | Energy_CZ05 | Demand_CZ05 | Energy_CZ06 | Demand_CZ06 | Energy_CZ07 | Demand_CZ07 | Energy_CZ08 | Demand_CZ08 | Energy_CZ09 | Demand_CZ09 | Energy_CZ10 | Demand_CZ10 | Energy_CZ11 | Demand_CZ11 | Energy_CZ12 | Demand_CZ12 | Energy_CZ13 | Demand_CZ13 | Energy_CZ14 | Demand_CZ14 | Energy_CZ15 | Demand_CZ15 | Energy_CZ16 | Demand_CZ16
J | V | Primary entrance to police station |  |  |  | Assembly | 0.95 | 0.97 | 1.03 | 1.19 | 1.02 | 1.18 | 1.05 | 1.19 | 1.03 | 1.17 | 1.12 | 1.27 | 1.1 | 1.22 | 1.13 | 1.23 | 1.12 | 1.26 | 1.09 | 1.22 | 1.05 | 1.18 | 1.04 | 1.18 | 1.05 | 1.17 | 1.07 | 1.14 | 1.19 | 1.2 | 0.98 | 1.15
K | W | Primary entrance to hospital or fire station |  |  |  | Primary School | 0.99 | 1.09 | 1.05 | 1 | 1.06 | 1 | 1.08 | 1.66 | 1.06 | 1.22 | 1.16 | 1.58 | 1.14 | 1.29 | 1.18 | 1.34 | 1.16 | 1.86 | 1.13 | 1.88 | 1.06 | 1 | 1.07 | 1 | 1.08 | 1 | 1.09 | 1.4 | 1.21 | 1.34 | 0.97 | 1
L | X | Primary entrance to emergency vehicle facilities |  |  |  | Secondary School | 0.97 | 1.03 | 1.04 | 1 | 1.04 | 1 | 1.06 | 1.21 | 1.04 | 1.22 | 1.14 | 1.43 | 1.12 | 1.26 | 1.16 | 1.31 | 1.15 | 1.84 | 1.12 | 1.77 | 1.07 | 1 | 1.06 | 1 | 1.08 | 1 | 1.09 | 1.47 | 1.21 | 1.3 | 0.98 | 1
Exterior |  | Drive-up windows |  |  |  | Community College | 1.03 | 1.09 | 1.09 | 1.21 | 1.08 | 1.13 | 1.1 | 1.44 | 1.08 | 1.23 | 1.16 | 1.27 | 1.14 | 1.25 | 1.17 | 1.28 | 1.16 | 1.31 | 1.15 | 1.29 | 1.12 | 1.44 | 1.11 | 1.28 | 1.13 | 1.55 | 1.12 | 1.33 | 1.24 | 1.34 | 1.06 | 1.22
AA |  | Vehicle service station uncovered fuel dispenser |  |  |  | University | 1.06 | 1.14 | 1.1 | 1.2 | 1.1 | 1.13 | 1.12 | 1.23 | 1.09 | 1.22 | 1.16 | 1.23 | 1.14 | 1.24 | 1.17 | 1.27 | 1.16 | 1.27 | 1.15 | 1.26 | 1.12 | 1.34 | 1.12 | 1.22 | 1.13 | 1.58 | 1.13 | 1.28 | 1.2 | 1.28 | 1.06 | 1.21
BB |  | Outdoor sales frontage |  |  |  | Relocatable Classroom | 0.97 | 1.07 | 1.01 | 1 | 1.01 | 1 | 1.04 | 1.22 | 1.01 | 1.31 | 1.12 | 1.67 | 1.13 | 1.26 | 1.11 | 1.29 | 1.11 | 1.29 | 1.11 | 1.31 | 1.04 | 1 | 1.04 | 1 | 1.05 | 1 | 1.09 | 1.33 | 1.19 | 1.31 | 0.99 | 1
CC |  | Hardscape ornamental lighting |  |  |  | Grocery | 0.8 | 0.75 | 0.9 | 1.2 | 0.86 | 1.16 | 0.92 | 1.24 | 0.86 | 1.16 | 1.03 | 1.2 | 1 | 1.17 | 1.05 | 1.25 | 1.06 | 1.27 | 1.05 | 1.28 | 0.99 | 1.28 | 0.96 | 1.28 | 1 | 1.31 | 1.05 | 1.32 | 1.13 | 1.3 | 0.87 | 1.25
DD |  | Building facades |  |  |  | Hospital | 1.07 | 1.1 | 1.1 | 1.18 | 1.11 | 1.15 | 1.11 | 1.21 | 1.09 | 1.17 | 1.16 | 1.26 | 1.15 | 1.23 | 1.17 | 1.26 | 1.17 | 1.28 | 1.14 | 1.27 | 1.11 | 1.23 | 1.11 | 1.23 | 1.12 | 1.24 | 1.13 | 1.28 | 1.19 | 1.29 | 1.06 | 1.2
EE |  | Outdoor sales lots |  |  |  | Nursing Home | 0.98 | 1.05 | 1.03 | 1.2 | 1.03 | 1.14 | 1.05 | 1.23 | 1.02 | 1.14 | 1.08 | 1.26 | 1.07 | 1.25 | 1.1 | 1.29 | 1.1 | 1.31 | 1.09 | 1.32 | 1.06 | 1.25 | 1.05 | 1.25 | 1.07 | 1.25 | 1.08 | 1.32 | 1.16 | 1.33 | 1 | 1.21
|  | Vehicle service station hardscape |  |  |  | Hotel | 0.91 | 1.14 | 0.98 | 1.22 | 1 | 1.2 | 1.02 | 1.24 | 0.99 | 1.21 | 1.09 | 1.27 | 1.1 | 1.24 | 1.11 | 1.28 | 1.1 | 1.29 | 1.07 | 1.29 | 1.02 | 1.25 | 1 | 1.25 | 1.03 | 1.26 | 1.03 | 1.3 | 1.16 | 1.29 | 0.9 | 1.23
|  | Vehicle service station canopies |  |  |  | Motel | 0.99 | 1.16 | 1.04 | 1.2 | 1.05 | 1.19 | 1.07 | 1.21 | 1.04 | 1.19 | 1.13 | 1.26 | 1.14 | 1.24 | 1.15 | 1.27 | 1.14 | 1.3 | 1.12 | 1.3 | 1.05 | 1.23 | 1.04 | 1.23 | 1.07 | 1.24 | 1.08 | 1.32 | 1.2 | 1.32 | 0.95 | 1.2
|  | Sales canopies |  |  |  | Bio/Tech Manuf. | 1.08 | 1.11 | 1.11 | 1.18 | 1.12 | 1.13 | 1.12 | 1.14 | 1.11 | 1.16 | 1.18 | 1.21 | 1.17 | 1.23 | 1.18 | 1.26 | 1.18 | 1.26 | 1.14 | 1.26 | 1.12 | 1.34 | 1.11 | 1.2 | 1.12 | 1.47 | 1.14 | 1.23 | 1.19 | 1.26 | 1.07 | 1.16
|  | Non-sales canopies |  |  |  | Light Industrial Manuf. | 0.98 | 1.08 | 1.04 | 1.16 | 1.04 | 1.11 | 1.05 | 1.14 | 1.04 | 1.15 | 1.11 | 1.19 | 1.08 | 1.19 | 1.11 | 1.2 | 1.11 | 1.22 | 1.08 | 1.21 | 1.04 | 1.15 | 1.04 | 1.18 | 1.05 | 1.16 | 1.06 | 1.2 | 1.15 | 1.29 | 0.98 | 1.15
|  | Guard stations |  |  |  | Large Office | 1.07 | 1.17 | 1.1 | 1.28 | 1.1 | 1.15 | 1.11 | 1.31 | 1.09 | 1.25 | 1.17 | 1.3 | 1.16 | 1.27 | 1.18 | 1.33 | 1.17 | 1.33 | 1.17 | 1.32 | 1.13 | 1.29 | 1.12 | 1.31 | 1.14 | 1.34 | 1.16 | 1.31 | 1.23 | 1.32 | 1.06 | 1.27
|  | Student pick-up/drop off zone |  |  |  | Small Office | 1 | 1.12 | 1.05 | 1.21 | 1.05 | 1.14 | 1.07 | 1.25 | 1.05 | 1.19 | 1.15 | 1.28 | 1.16 | 1.25 | 1.16 | 1.28 | 1.15 | 1.32 | 1.13 | 1.29 | 1.07 | 1.28 | 1.07 | 1.23 | 1.07 | 1.26 | 1.11 | 1.3 | 1.21 | 1.3 | 1 | 1.21
|  | Outdoor dining |  |  |  | Sit-Down Restaurant | 0.96 | 0.99 | 1.04 | 1.2 | 1.02 | 1.17 | 1.06 | 1.19 | 1.03 | 1.18 | 1.11 | 1.28 | 1.12 | 1.26 | 1.12 | 1.24 | 1.11 | 1.26 | 1.09 | 1.23 | 1.04 | 1.19 | 1.03 | 1.18 | 1.04 | 1.19 | 1.07 | 1.16 | 1.17 | 1.26 | 0.95 | 1.16
|  | Special security lighting for retail parking |  |  |  | Fast-Food Restaurant | 0.97 | 1.03 | 1.03 | 1.16 | 1.02 | 1.13 | 1.05 | 1.17 | 1.02 | 1.14 | 1.09 | 1.24 | 1.12 | 1.22 | 1.11 | 1.22 | 1.11 | 1.24 | 1.09 | 1.22 | 1.05 | 1.18 | 1.05 | 1.18 | 1.06 | 1.18 | 1.07 | 1.23 | 1.15 | 1.23 | 0.98 | 1.16
|  | Special security lighting for pedestrian walkway |  |  |  | Department Store | 0.96 | 1.07 | 1.05 | 1.22 | 1.06 | 1.24 | 1.08 | 1.24 | 1.06 | 1.21 | 1.16 | 1.24 | 1.15 | 1.21 | 1.17 | 1.22 | 1.15 | 1.25 | 1.13 | 1.23 | 1.07 | 1.19 | 1.07 | 1.21 | 1.08 | 1.2 | 1.09 | 1.21 | 1.17 | 1.24 | 0.98 | 1.17
[6 empty] | Big Box Retail | 0.97 | 1.08 | 1.05 | 1.22 | 1.06 | 1.23 | 1.07 | 1.23 | 1.05 | 1.22 | 1.15 | 1.25 | 1.14 | 1.22 | 1.15 | 1.24 | 1.14 | 1.27 | 1.12 | 1.25 | 1.06 | 1.2 | 1.06 | 1.2 | 1.07 | 1.21 | 1.09 | 1.26 | 1.17 | 1.26 | 0.97 | 1.16
[6 empty] | Small Retail | 0.97 | 1.1 | 1.04 | 1.21 | 1.04 | 1.2 | 1.06 | 1.23 | 1.04 | 1.2 | 1.14 | 1.23 | 1.13 | 1.21 | 1.15 | 1.23 | 1.14 | 1.26 | 1.12 | 1.24 | 1.06 | 1.19 | 1.06 | 1.2 | 1.07 | 1.2 | 1.09 | 1.2 | 1.17 | 1.24 | 0.99 | 1.17
[6 empty] | Conditioned Storage | 0.85 | 0.91 | 0.96 | 1.2 | 0.92 | 1.04 | 0.98 | 1.25 | 0.92 | 1.15 | 1.03 | 1.32 | 1.01 | 1.27 | 1.05 | 1.32 | 1.04 | 1.34 | 1.04 | 1.31 | 0.98 | 1.21 | 0.98 | 1.25 | 0.99 | 1.22 | 1.01 | 1.29 | 1.11 | 1.3 | 0.89 | 1.21
[6 empty] | Unconditioned Storage | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  | space_type_list_2 |  |  |  | Refrigerated Warehouse | 1.6 | 1.74 | 1.62 | 1.32 | 1.62 | 1.32 | 1.62 | 1.3 | 1.59 | 1.31 | 1.58 | 1.34 | 1.62 | 1.35 | 1.6 | 1.25 | 1.59 | 1.26 | 1.58 | 1.26 | 1.55 | 1.25 | 1.57 | 1.32 | 1.56 | 1.25 | 1.52 | 1.32 | 1.63 | 1.26 | 1.39 | 1.26
|  | Assembly |  |  |  | Exterior | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Grocery
|  | Hospital |  |  |  | 1 | CFL and non-CFL data from DEER: 'DEER-Lighting_IE_Factors_9Sept2013'
|  | Hotel |  |  |  | 2 | Climate zones that are served by more than one IOU have different interactive effects for each IOU
|  | Manufacturing |  |  |  | 3 | Where a climate zone is served by more than one IOU, the order of precedence for interactive effects used in this table is ; PG&E, SCE, SDGE
Manufacturing - hi-tech
|  | Motel |  |  |  | CDF_table
|  | Nursing home |  |  |  | Coincident Demand Factor
Office
|  | Other |  |  |  | Building Type | CZ01 | CZ02 | CZ03 | CZ04 | CZ05 | CZ06 | CZ07 | CZ08 | CZ09 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16
|  | Outdoor lighting |  |  |  | Assembly | 0.53 | 0.53 | 0.53 | 0.532 | 0.532 | 0.53 | 0.53 | 0.53 | 0.53 | 0.53 | 0.53 | 0.53 | 0.53 | 0.53 | 0.53 | 0.53
|  | Refrigerated space |  |  |  | Primary School | 0.62 | 0.02 | 0.02 | 0.02 | 0.617 | 0.02 | 0.62 | 0.62 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
|  | Restaurant |  |  |  | Secondary School | 0.71 | 0.02 | 0.02 | 0.02 | 0.709 | 0.02 | 0.71 | 0.71 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
|  | Restroom/hallway/small storage |  |  |  | Community College | 0.81 | 0.49 | 0.49 | 0.487 | 0.806 | 0.49 | 0.81 | 0.81 | 0.49 | 0.49 | 0.49 | 0.49 | 0.02 | 0.49 | 0.49 | 0.49
|  | Retail |  |  |  | University | 0.72 | 0.44 | 0.44 | 0.439 | 0.72 | 0.44 | 0.72 | 0.72 | 0.44 | 0.44 | 0.44 | 0.44 | 0.03 | 0.44 | 0.44 | 0.44
|  | School |  |  |  | Relocatable Classroom | 0.7 | 0.02 | 0.02 | 0.02 | 0.702 | 0.02 | 0.7 | 0.7 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
|  | School - University |  |  |  | Grocery | 0.69 | 0.69 | 0.69 | 0.69 | 0.69 | 0.69 | 0.69 | 0.69 | 0.69 | 0.69 | 0.69 | 0.69 | 0.69 | 0.69 | 0.69 | 0.69
|  | Storage with htg or clg |  |  |  | Hospital | 0.83 | 0.83 | 0.83 | 0.827 | 0.827 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83
|  | Storage without htg or clg |  |  |  | Nursing Home | 0.68 | 0.68 | 0.68 | 0.677 | 0.677 | 0.68 | 0.68 | 0.68 | 0.68 | 0.68 | 0.68 | 0.68 | 0.68 | 0.68 | 0.68 | 0.68
[6 empty] | Hotel | 0.24 | 0.24 | 0.24 | 0.242 | 0.242 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.24
|  | Range name:hour |  |  |  | Motel | 0.17 | 0.17 | 0.17 | 0.172 | 0.172 | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.17 | 0.17
|  | Off |  |  |  | Bio/Tech Manuf. | 0.85 | 0.85 | 0.85 | 0.851 | 0.851 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85
|  | 0:00 |  |  |  | Light Industrial Manuf. | 0.92 | 0.92 | 0.92 | 0.923 | 0.923 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92 | 0.92
|  | 0:15 |  |  |  | Large Office | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71
|  | 0:30 |  |  |  | Small Office | 0.69 | 0.69 | 0.69 | 0.693 | 0.693 | 0.69 | 0.69 | 0.69 | 0.69 | 0.69 | 0.69 | 0.69 | 0.69 | 0.69 | 0.69 | 0.69
|  | 0:45 |  |  |  | Sit-Down Restaurant | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
|  | 1:00 |  |  |  | Fast-Food Restaurant | 0.81 | 0.81 | 0.81 | 0.813 | 0.813 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81 | 0.81
|  | 1:15 |  |  |  | Department Store | 0.76 | 0.76 | 0.76 | 0.759 | 0.759 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76
|  | 1:30 |  |  |  | Big Box Retail | 0.85 | 0.85 | 0.85 | 0.848 | 0.848 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85
|  | 1:45 |  |  |  | Small Retail | 0.88 | 0.88 | 0.88 | 0.875 | 0.875 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88
|  | 2:00 |  |  |  | Conditioned Storage | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
|  | 2:15 |  |  |  | Unconditioned Storage | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
|  | 2:30 |  |  |  | Refrigerated Warehouse | 0.56 | 0.56 | 0.56 | 0.556 | 0.556 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56
|  | 2:45 |  |  |  | Exterior | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 3:00 |  |  |  | 1 | CZ01: Non-CFL CDF from DEER: 'DEER-Lighting_IE_Factors_9Sept2013'
3:15
3:30
|  | 3:45 |  |  |  | Therms_table
|  | 4:00 |  |  |  | HVAC interactive effects - natural gas (therms/kWh) | bar: CZ01 to CZ02
4:15
|  | 4:30 |  |  |  | Building Type | CZ01 | CZ02 | CZ03 | CZ04 | CZ05 | CZ06 | CZ07 | CZ08 | CZ09 | CZ10 | CZ11 | CZ12 | CZ13 | CZ14 | CZ15 | CZ16
|  | 4:45 |  |  |  | Assembly | -0.015 | -0.0099 | -0.0096 | -0.0083 | -0.0075 | -0.0051 | -0.0038 | -0.0041 | -0.0039 | -0.0048 | -0.009 | -0.009 | -0.0073 | -0.0081 | -0.0018 | -0.014
|  | 5:00 |  |  |  | Primary School | -0.015 | -0.01 | -0.0085 | -0.0079 | -0.0069 | -0.0037 | -0.0034 | -0.0033 | -0.0033 | -0.0041 | -0.0096 | -0.0094 | -0.0071 | -0.0082 | -0.0014 | -0.019
|  | 5:15 |  |  |  | Secondary School | -0.018 | -0.012 | -0.011 | -0.0098 | -0.0091 | -0.0058 | -0.0046 | -0.0048 | -0.0048 | -0.0053 | -0.011 | -0.011 | -0.0098 | -0.0096 | -0.0023 | -0.019
|  | 5:30 |  |  |  | Community College | -0.017 | -0.012 | -0.011 | -0.0097 | -0.0098 | -0.0057 | -0.0047 | -0.005 | -0.0051 | -0.0048 | -0.011 | -0.011 | -0.0085 | -0.0086 | -0.0024 | -0.019
|  | 5:45 |  |  |  | University | -0.011 | -0.0085 | -0.0076 | -0.0069 | -0.0069 | -0.0043 | -0.004 | -0.004 | -0.0045 | -0.0039 | -0.008 | -0.0079 | -0.0063 | -0.0061 | -0.0023 | -0.015
|  | 6:00 |  |  |  | Relocatable Classroom | -0.014 | -0.011 | -0.0098 | -0.009 | -0.0087 | -0.0054 | -0.0054 | -0.0053 | -0.0055 | -0.0058 | -0.011 | -0.01 | -0.0079 | -0.0079 | -0.0031 | -0.017
|  | 6:15 |  |  |  | Grocery | -0.018 | -0.013 | -0.015 | -0.013 | -0.014 | -0.014 | -0.013 | -0.012 | -0.011 | -0.011 | -0.011 | -0.012 | -0.0099 | -0.012 | -0.0066 | -0.015
|  | 6:30 |  |  |  | Hospital | -0.0075 | -0.0066 | -0.006 | -0.0059 | -0.0061 | -0.0051 | -0.0049 | -0.005 | -0.0049 | -0.0054 | -0.0065 | -0.0064 | -0.0056 | -0.0068 | -0.0045 | -0.011
|  | 6:45 |  |  |  | Nursing Home | -0.018 | -0.015 | -0.014 | -0.013 | -0.013 | -0.01 | -0.0095 | -0.0096 | -0.0097 | -0.0098 | -0.013 | -0.013 | -0.011 | -0.012 | -0.0064 | -0.019
|  | 7:00 |  |  |  | Hotel | -0.0072 | -0.006 | -0.0056 | -0.0049 | -0.0052 | -0.0033 | -0.003 | -0.0032 | -0.0032 | -0.0033 | -0.0058 | -0.0057 | -0.0045 | -0.0046 | -0.0021 | -0.0094
|  | 7:15 |  |  |  | Motel | -0.0087 | -0.0065 | -0.0059 | -0.0053 | -0.0058 | -0.0032 | -0.0029 | -0.0028 | -0.0029 | -0.0033 | -0.0059 | -0.006 | -0.0048 | -0.0044 | -0.0016 | -0.0095
|  | 7:30 |  |  |  | Bio/Tech Manuf. | -0.0008 | -0.0006 | -0.0005 | -0.0004 | -0.0003 | -0.0002 | 0 | -0.0002 | 0 | -0.0003 | -0.0009 | -0.0007 | -0.0005 | -0.0009 | 0 | -0.0033
|  | 7:45 |  |  |  | Light Industrial Manuf. | -0.009 | -0.0057 | -0.0049 | -0.0047 | -0.0036 | -0.0019 | -0.0014 | -0.0015 | -0.0013 | -0.0016 | -0.0065 | -0.0061 | -0.0046 | -0.0057 | -0.0008 | -0.012
|  | 8:00 |  |  |  | Large Office | -0.0085 | -0.0071 | -0.0064 | -0.0056 | -0.0058 | -0.0045 | -0.0021 | -0.0043 | -0.0061 | -0.003 | -0.0077 | -0.0068 | -0.0058 | -0.0061 | -0.003 | -0.013
|  | 8:15 |  |  |  | Small Office | -0.0049 | -0.004 | -0.0031 | -0.0028 | -0.002 | -0.0013 | -0.0004 | -0.0013 | -0.0014 | -0.0012 | -0.005 | -0.0043 | -0.0033 | -0.003 | -0.0006 | -0.0087
|  | 8:30 |  |  |  | Sit-Down Restaurant | -0.013 | -0.0093 | -0.0093 | -0.0077 | -0.008 | -0.0063 | -0.0054 | -0.0052 | -0.0046 | -0.0054 | -0.0085 | -0.0085 | -0.0067 | -0.009 | -0.0024 | -0.014
|  | 8:45 |  |  |  | Fast-Food Restaurant | -0.011 | -0.008 | -0.0081 | -0.0069 | -0.0075 | -0.006 | -0.0054 | -0.0051 | 0.0048 | -0.0054 | -0.0074 | -0.0073 | -0.0059 | -0.0079 | -0.0027 | -0.013
|  | 9:00 |  |  |  | Department Store | -0.009 | -0.0056 | -0.0043 | -0.0037 | -0.0021 | -0.0007 | -0.0004 | -0.0009 | -0.0006 | -0.001 | -0.0066 | -0.006 | -0.0045 | -0.0051 | -0.0003 | -0.012
|  | 9:15 |  |  |  | Big Box Retail | -0.011 | -0.0071 | -0.0058 | -0.005 | -0.0043 | -0.0023 | -0.0016 | -0.0022 | -0.0018 | -0.0024 | -0.0071 | -0.0065 | -0.0049 | -0.0059 | -0.0009 | -0.014
|  | 9:30 |  |  |  | Small Retail | -0.0093 | -0.006 | -0.0049 | -0.0039 | -0.0031 | -0.0013 | -0.0009 | -0.0012 | -0.001 | -0.0013 | -0.0065 | -0.0061 | -0.0044 | -0.0045 | -0.0004 | -0.012
|  | 9:45 |  |  |  | Conditioned Storage | -0.015 | -0.0086 | -0.0091 | -0.0077 | -0.0077 | -0.0057 | -0.004 | -0.0042 | -0.0042 | -0.0043 | -0.0079 | -0.0079 | -0.0066 | -0.0078 | -0.0022 | -0.012
|  | 10:00 |  |  |  | Unconditioned Storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 10:15 |  |  |  | Refrigerated Warehouse | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.0004
|  | 10:30 |  |  |  | Exterior | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 10:45 |  |  |  | 1 | CZ01: Therm IE data from DEER (Dec 2011)
|  | 11:00 |  |  |  | 2 | CZ01: Values are for existing buildings
11:15
11:30
11:45
12:00
12:15
12:30
12:45
13:00
13:15
13:30
13:45
14:00
14:15
14:30
14:45
15:00
15:15
15:30
15:45
16:00
16:15
16:30
16:45
17:00
17:15
17:30
17:45
18:00
18:15
18:30
18:45
19:00
19:15
19:30
19:45
20:00
20:15
20:30
20:45
21:00
21:15
21:30
21:45
22:00
22:15
22:30
22:45
23:00
23:15
23:30
23:45
24 hrs

## Reference data
Lighting Control Savings Factors
Space Type | Occupancy Sensor, Wall or Ceiling Mounted | Daylight Sensor | Combined Occupancy & Daylight Sensors | Manual bi-level switch-only an option for pre-existing controls | DEER 2011 Default Operating Hrs |  | 2013 Title 24 Motion Sensor Savings Factor
Assembly | 36% | 36% | 40% | 35% | Building Type | ophrs | Dimming to 40%-80% of full power or continuous dimming required
Break Room | 20% | 20% | 40% | 35% | Assembly | 2610 | Average dimming level assumed: |  | 50%
Classroom | 18% | 29% | 34% | 6% | Primary School | 2140
Computer Room | 35% | NA | 34% | 6% | Secondary School | 2280 | Operating hours: |  | 4180 | hrs
Conference | 35% | 18% | 40% | 35% | Community College | 2420 | % time at full power: | 67% | 2801 | hrs
Dining | 35% | 18% | 40% | 6% | University | 2350 | % time dimmed: | 33% | 1379 | hrs
Gymnasium | 35% | 35% | 40% | 6% | Relocatable Classroom | 2480
Hallway | 15% | 15% | NA | NA | Grocery | 4910 | Savings factor:
Hospital Room | 45% | NA | NA | 6% | Hospital | 5260 | % full power = | 67% x 100% | 0.67
Industrial | 45% | NA | NA | 6% | Nursing Home | 4160 | % dimmed power = 33% x 50% |  | 0.165
Kitchen | 30% | NA | NA | 6% | Hotel | 1950 | Equivalent run time factor |  | 0.835
Library | 15% | 18% | 34% | 6% | Motel | 1550 | Savings factor: |  | 16.5%
Lobby | 25% | 18% | 40% | 6% | Bio/Tech Manuf. | 3530 | Equivalent full load hrs (ELFH) |  | 3490.3
Lodging (guest rooms) | 45% | NA | 40% | 6% | Light Industrial Manuf. | 3220
Open Office | 22% | 27% | 40% | 35% | Large Office | 2640
Parking Garage | 15% | 18% | 40% | 35% | Small Office | 2590
Private Office | 22% | 27% | 40% | 35% | Sit-Down Restaurant | 4830
Process | 45% | NA | 40% | 6% | Fast-Food Restaurant | 4840
Public Assembly | 36% | 36% | 40% | 6% | Department Store | 3380
Restroom | 40% | NA | 40% | NA | Big Box Retail | 4270
Retail | 15% | 29% | 34% | 6% | Small Retail | 3380
Stairs | 25% | NA | NA | NA | Conditioned Storage | 3420
Storage | 45% | NA | 40% | 35% | Unconditioned Storage | 3420
Technical Area | 35% | 18% | 40% | 6% | Refrigerated Warehouse | 4770
Warehouses | 31% | 28% | 40% | 35%
Other | 7% | 18% | 34% | 6%
Data Source Color Code for Controls
LBNL | Black
LBNL-expanded to space type | Red
CA SPC Manual | Blue
EMaine TRM | Green
Linear Fluorescent & High-Bay Fixtures |  |  | Compact Fluorescent Lamps
Building Type | Operating Hours |  | Building Type | Operating Hours
Assembly | 2610 |  | Assembly | 2300
Primary School | 2140 |  | Primary School | 2240
Secondary School | 2280 |  | Secondary School | 2330
Community College | 2420 |  | Community College | 2420
University | 2350 |  | University | 2370
Relocatable Classroom | 2480 |  | Relocatable Classroom | 2600
Grocery | 4910 |  | Grocery | 3890
Hospital | 5260 |  | Hospital | 4200
Nursing Home | 4160 |  | Nursing Home | 3570
Hotel | 1950 |  | Hotel | 1670
Motel | 1550 |  | Motel | 1370
Bio/Tech Manuf. | 3530 |  | Bio/Tech Manuf. | 3090
Light Industrial Manuf. | 3220 |  | Light Industrial Manuf. | 2580
Large Office | 2640 |  | Large Office | 3000
Small Office | 2590 |  | Small Office | 2980
Sit-Down Restaurant | 4830 |  | Sit-Down Restaurant | 4830
Fast-Food Restaurant | 4840 |  | Fast-Food Restaurant | 4810
Department Store | 3380 |  | Department Store | 3710
Big Box Retail | 4270 |  | Big Box Retail | 4350
Small Retail | 3380 |  | Small Retail | 4010
Conditioned Storage | 3420 |  | Conditioned Storage | 2760
Unconditioned Storage | 3420 |  | Unconditioned Storage | 2760
Refrigerated Warehouse | 4770 |  | Refrigerated Warehouse | 4730
Notes:
All data are from the DEER Measure Database Updates (Version 4.00 first release in November 2011)